## Project Information
Project name | Colorado Green (example data subset)
Project owner | Iberdrola Renewables / Shell WindEnergy
Project number (if applicable) | N/A
Name of person & organization completing form | Example author
Date when form was completed | 2022-03-27
Revision number | 0
Reason for revision | First issue
Country & state | Colorado, USA
Turbine Coordinates Datum | WGS84
Turbine Coordinates Projection | UTM
Accompanying report file name | ColoradoGreenSS_Rev00.pdf
Accompanying report revision number | Rev00
DEF version | 1.1

## Turbine Layout Summary
Project Name | Wind Turbine ID | Easting or Longitude | Northing or Latitude | Ground Elevation Above Sea Level (m) | Wind Turbine Manufacturer | Wind Turbine Model | Wind Turbine Rated Power (MW) | Rotor Diameter (m) [D] | Hub Height (m) [Zhub] | Associated Data Source | Ve50 (3-sec, 50 year) (m/s) | V50 (10-min, 50 year) (m/s) | COV (if applicable) | Air Density (kg/m3) [ρ] | Annual Average Wind Speed at Hub Height (m/s) [Vave] | Scale Parameter of Weibull Function (m/s) [C] | Shape Parameter of Weibull Function (-) [k] | Turbulence Structure Correction Parameter (-)[CCT] | Annual Mean Wind Shear (-) | Annual Average Turbulence Intensity at 15 m/s (%) [TI15] | Standard Deviation of Turbulence Intensity at 15 m/s (%) [σI] | Inflow Angle (°)
Colorado Green | 97 | -102.595 | 37.7145 | 1336 | GE | GE 1.6-91 | 1.6 | 91 | 80 | Gobblers Knob East | 59.57 | 42.55 | N/A | 1.0667 | 8.5 | 9.609 | 2.34 | 1.05 | 0.14 | 9.726% | 4.082% | 0.1
Colorado Green | 98 | -102.601 | 37.7145 | 1341 | GE | GE 1.6-91 | 1.6 | 91 | 80 | Gobblers Knob East | 59.43 | 42.45 | N/A | 1.066 | 8.5 | 9.587 | 2.34 | 1.05 | 0.14 | 9.774% | 4.07% | 0.1
Colorado Green | 100 | -102.598 | 37.7145 | 1339 | GE | GE 1.6-91 | 1.6 | 91 | 80 | Gobblers Knob East | 59.36 | 42.4 | N/A | 1.066 | 8.5 | 9.576 | 2.34 | 1.05 | 0.14 | 9.628% | 3.822% | 0
Colorado Green | 102 | -102.612 | 37.7156 | 1344 | GE | GE 1.6-91 | 1.6 | 91 | 80 | Gobblers Knob East | 59.43 | 42.45 | N/A | 1.066 | 8.5 | 9.587 | 2.34 | 1.05 | 0.14 | 9.774% | 4.07% | 0
Colorado Green | 103 | -102.623 | 37.7156 | 1345 | GE | GE 1.6-91 | 1.6 | 91 | 80 | Gobblers Knob West | 59.36 | 42.4 | N/A | 1.066 | 8.49 | 9.51 | 2.41 | 1.05 | 0.2 | 9.628% | 3.822% | 0.1
Colorado Green | 104 | -102.62 | 37.7156 | 1347 | GE | GE 1.6-91 | 1.6 | 91 | 80 | Gobblers Knob West | 59.43 | 42.45 | N/A | 1.066 | 8.49 | 9.521 | 2.41 | 1.05 | 0.2 | 9.774% | 4.07% | 0.1
Colorado Green | 105 | -102.617 | 37.7156 | 1346 | GE | GE 1.6-91 | 1.6 | 91 | 80 | Gobblers Knob West | 59.29 | 42.35 | N/A | 1.066 | 8.49 | 9.499 | 2.41 | 1.05 | 0.2 | 9.754% | 4.133% | 0.1
Colorado Green | 106 | -102.615 | 37.7156 | 1345 | GE | GE 1.6-91 | 1.6 | 91 | 80 | Gobblers Knob West | 59.29 | 42.35 | N/A | 1.066 | 8.49 | 9.499 | 2.41 | 1.05 | 0.2 | 9.754% | 4.133% | 0
Colorado Green | 107 | -102.609 | 37.7156 | 1343 | GE | GE 1.6-91 | 1.6 | 91 | 80 | Gobblers Knob East | 59.57 | 42.55 | N/A | 1.066 | 8.5 | 9.609 | 2.34 | 1.05 | 0.14 | 9.726% | 4.082% | 0.1
Colorado Green | 108 | -102.606 | 37.7156 | 1344 | GE | GE 1.6-91 | 1.6 | 91 | 80 | Gobblers Knob East | 59.36 | 42.4 | N/A | 1.066 | 8.5 | 9.576 | 2.34 | 1.05 | 0.14 | 9.628% | 3.822% | 0.1

## Measurement Device Summary
Measurement device ID | Easting or Longitude | Northing or Latitude | Ground Elevation Above Sea Level (m) | Measurement device height (m)
Gobblers Knob West | 37.675 | -102.6958 | 1375 | 40
Gobblers Knob East | 37.775 | -102.55 | 1314 | 40

## WS Frequency
Annual Wind Speed Frequency Distribution (%)
|  | Measurement Device |  |  |  | Wind Turbine
Wind Direction (Midpoint) (°) | Wind Speed (Midpoint) (m/s) | Gobblers Knob West | Number of samples | Gobblers Knob East | Number of samples | 97 | 98 | 100 | 102 | 103 | 104 | 105 | 106 | 107 | 108
0 | 0 | 0.01142% | 2 | 0.01142% | 2 | 0.01142% | 0.01142% | 0.01142% | 0.01142% | 0.01142% | 0.01142% | 0.01142% | 0.01142% | 0.01142% | 0.01142%
0 | 1 | 0.1541% | 27 | 0.05137% | 9 | 0.05137% | 0.05137% | 0.05137% | 0.05137% | 0.1541% | 0.1541% | 0.1541% | 0.1541% | 0.05137% | 0.05137%
0 | 2 | 0.354% | 62 | 0.2283% | 40 | 0.2112% | 0.2283% | 0.2283% | 0.2283% | 0.354% | 0.354% | 0.354% | 0.354% | 0.2112% | 0.2283%
0 | 3 | 0.4853% | 85 | 0.3539% | 62 | 0.371% | 0.3539% | 0.3539% | 0.3539% | 0.4853% | 0.451% | 0.4853% | 0.4853% | 0.371% | 0.3539%
0 | 4 | 0.6508% | 114 | 0.4909% | 86 | 0.4909% | 0.4909% | 0.4909% | 0.4909% | 0.6508% | 0.6851% | 0.6508% | 0.6508% | 0.4909% | 0.4909%
0 | 5 | 0.6451% | 113 | 0.5308% | 93 | 0.5308% | 0.5308% | 0.5308% | 0.5308% | 0.6451% | 0.6451% | 0.6451% | 0.6451% | 0.5308% | 0.5308%
0 | 6 | 0.7079% | 124 | 0.5479% | 96 | 0.5479% | 0.5479% | 0.5479% | 0.5479% | 0.7079% | 0.6965% | 0.7079% | 0.7079% | 0.5479% | 0.5479%
0 | 7 | 0.7593% | 133 | 0.5594% | 98 | 0.5537% | 0.5537% | 0.5537% | 0.5537% | 0.7593% | 0.7707% | 0.7593% | 0.7593% | 0.5537% | 0.5537%
0 | 8 | 0.7251% | 127 | 0.411% | 72 | 0.3995% | 0.3995% | 0.4167% | 0.3995% | 0.7251% | 0.7251% | 0.7251% | 0.7251% | 0.3995% | 0.4167%
0 | 9 | 0.5195% | 91 | 0.4452% | 78 | 0.4566% | 0.4566% | 0.4452% | 0.4566% | 0.5195% | 0.5195% | 0.5195% | 0.5195% | 0.4566% | 0.4452%
0 | 10 | 0.5309% | 93 | 0.4852% | 85 | 0.4909% | 0.4909% | 0.4852% | 0.4909% | 0.5309% | 0.4567% | 0.5309% | 0.5309% | 0.4909% | 0.4852%
0 | 11 | 0.4168% | 73 | 0.3368% | 59 | 0.3368% | 0.3368% | 0.3368% | 0.3368% | 0.4168% | 0.491% | 0.4168% | 0.4168% | 0.3368% | 0.3368%
0 | 12 | 0.4168% | 73 | 0.3082% | 54 | 0.3025% | 0.3082% | 0.3082% | 0.3082% | 0.4168% | 0.4168% | 0.4168% | 0.4168% | 0.3025% | 0.3082%
0 | 13 | 0.2797% | 49 | 0.2055% | 36 | 0.1998% | 0.2055% | 0.2055% | 0.2055% | 0.2797% | 0.2797% | 0.2797% | 0.2797% | 0.1998% | 0.2055%
0 | 14 | 0.2169% | 38 | 0.1826% | 32 | 0.1884% | 0.1769% | 0.1826% | 0.1769% | 0.2169% | 0.2169% | 0.2169% | 0.2169% | 0.1884% | 0.1826%
0 | 15 | 0.1713% | 30 | 0.0742% | 13 | 0.0742% | 0.0742% | 0.06849% | 0.0742% | 0.1599% | 0.1599% | 0.1713% | 0.1713% | 0.0742% | 0.06849%
0 | 16 | 0.07993% | 14 | 0.04566% | 8 | 0.05137% | 0.05137% | 0.05137% | 0.05137% | 0.09135% | 0.09135% | 0.07993% | 0.07993% | 0.05137% | 0.05137%
0 | 17 | 0.05138% | 9 | 0.03995% | 7 | 0.03425% | 0.03995% | 0.03995% | 0.03995% | 0.05138% | 0.05138% | 0.05138% | 0.05138% | 0.03425% | 0.03995%
0 | 18 | 0.02855% | 5 | 0.02854% | 5 | 0.03425% | 0.02854% | 0.02854% | 0.02854% | 0.02855% | 0.02855% | 0.02855% | 0.02855% | 0.03425% | 0.02854%
0 | 19 | 0.04567% | 8 | 0.005708% | 1 | 0.005708% | 0.005708% | 0.005708% | 0.005708% | 0.03996% | 0.03996% | 0.04567% | 0.04567% | 0.005708% | 0.005708%
0 | 20 | 0.02284% | 4 | 0.02854% | 5 | 0.02854% | 0.02854% | 0.02854% | 0.02854% | 0.02855% | 0.02855% | 0.02284% | 0.02284% | 0.02854% | 0.02854%
0 | 21 | 0.005709% | 1 | 0.01712% | 3 | 0.01712% | 0.01712% | 0.01712% | 0.01712% | 0.005709% | 0.005709% | 0.005709% | 0.005709% | 0.01712% | 0.01712%
0 | 22 | 0.01142% | 2 | 0.005708% | 1 | 0.005708% | 0.005708% | 0.005708% | 0.005708% | 0.01142% | 0.01142% | 0.01142% | 0.01142% | 0.005708% | 0.005708%
0 | 23 | 0.005709% | 1 | 0% | 0 | 0% | 0% | 0% | 0% | 0.005709% | 0.005709% | 0.005709% | 0.005709% | 0% | 0%
0 | 24 | 0.01713% | 3 | 0% | 0 | 0% | 0% | 0% | 0% | 0.01713% | 0.01713% | 0.01713% | 0.01713% | 0% | 0%
0 | 25 | 0.01713% | 3 | 0% | 0 | 0% | 0% | 0% | 0% | 0.01713% | 0.01713% | 0.01713% | 0.01713% | 0% | 0%
0 | 26 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
0 | 27 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
0 | 28 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
0 | 29 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
0 | 30 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
0 | 31 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
0 | 32 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
0 | 33 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
0 | 34 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
0 | 35 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
0 | 36 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
0 | 37 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
0 | 38 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
0 | 39 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
0 | 40 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
30 | 0 | 0.01142% | 2 | 0.005708% | 1 | 0.005708% | 0.005708% | 0.005708% | 0.005708% | 0.01142% | 0.01142% | 0.01142% | 0.01142% | 0.005708% | 0.005708%
30 | 1 | 0.137% | 24 | 0.06849% | 12 | 0.06849% | 0.06849% | 0.06849% | 0.06849% | 0.137% | 0.137% | 0.137% | 0.137% | 0.06849% | 0.06849%
30 | 2 | 0.3825% | 67 | 0.2226% | 39 | 0.1998% | 0.2226% | 0.2226% | 0.2226% | 0.3825% | 0.3825% | 0.3825% | 0.3825% | 0.1998% | 0.2226%
30 | 3 | 0.4624% | 81 | 0.3196% | 56 | 0.3425% | 0.3196% | 0.3196% | 0.3196% | 0.4624% | 0.4282% | 0.4624% | 0.4624% | 0.3425% | 0.3196%
30 | 4 | 0.4396% | 77 | 0.3881% | 68 | 0.3881% | 0.3881% | 0.3881% | 0.3881% | 0.4396% | 0.4739% | 0.4396% | 0.4396% | 0.3881% | 0.3881%
30 | 5 | 0.5309% | 93 | 0.5251% | 92 | 0.5251% | 0.5251% | 0.5251% | 0.5251% | 0.5309% | 0.5309% | 0.5309% | 0.5309% | 0.5251% | 0.5251%
30 | 6 | 0.5652% | 99 | 0.645% | 113 | 0.6336% | 0.6393% | 0.6393% | 0.6393% | 0.5652% | 0.5652% | 0.5652% | 0.5652% | 0.6336% | 0.6393%
30 | 7 | 0.4796% | 84 | 0.5936% | 104 | 0.5993% | 0.5936% | 0.5993% | 0.5936% | 0.4796% | 0.4796% | 0.4796% | 0.4796% | 0.5993% | 0.5993%
30 | 8 | 0.4567% | 80 | 0.3938% | 69 | 0.371% | 0.371% | 0.3938% | 0.371% | 0.451% | 0.451% | 0.4567% | 0.4567% | 0.371% | 0.3938%
30 | 9 | 0.354% | 62 | 0.3824% | 67 | 0.411% | 0.411% | 0.3824% | 0.411% | 0.3597% | 0.3597% | 0.354% | 0.354% | 0.411% | 0.3824%
30 | 10 | 0.3026% | 53 | 0.3196% | 56 | 0.3025% | 0.3082% | 0.3196% | 0.3082% | 0.3026% | 0.274% | 0.3026% | 0.3026% | 0.3025% | 0.3196%
30 | 11 | 0.177% | 31 | 0.3425% | 60 | 0.3539% | 0.3539% | 0.3425% | 0.3539% | 0.177% | 0.2055% | 0.177% | 0.177% | 0.3539% | 0.3425%
30 | 12 | 0.177% | 31 | 0.2683% | 47 | 0.2683% | 0.2626% | 0.2626% | 0.2626% | 0.177% | 0.177% | 0.177% | 0.177% | 0.2683% | 0.2626%
30 | 13 | 0.1199% | 21 | 0.1769% | 31 | 0.1769% | 0.1826% | 0.1826% | 0.1826% | 0.1199% | 0.1199% | 0.1199% | 0.1199% | 0.1769% | 0.1826%
30 | 14 | 0.05138% | 9 | 0.1256% | 22 | 0.1199% | 0.1199% | 0.1256% | 0.1199% | 0.05138% | 0.05138% | 0.05138% | 0.05138% | 0.1199% | 0.1256%
30 | 15 | 0.02284% | 4 | 0.08562% | 15 | 0.06849% | 0.06849% | 0.06279% | 0.06849% | 0.02284% | 0.02284% | 0.02284% | 0.02284% | 0.06849% | 0.06279%
30 | 16 | 0.02284% | 4 | 0.04566% | 8 | 0.06849% | 0.06279% | 0.06279% | 0.06279% | 0.02284% | 0.02284% | 0.02284% | 0.02284% | 0.06849% | 0.06279%
30 | 17 | 0.01713% | 3 | 0.02283% | 4 | 0.02283% | 0.02283% | 0.02854% | 0.02283% | 0.01713% | 0.01713% | 0.01713% | 0.01713% | 0.02283% | 0.02854%
30 | 18 | 0.01713% | 3 | 0.02283% | 4 | 0.02854% | 0.02854% | 0.02283% | 0.02854% | 0% | 0% | 0% | 0% | 0.02854% | 0.02283%
30 | 19 | 0% | 0 | 0.005708% | 1 | 0.005708% | 0.005708% | 0.005708% | 0.005708% | 0% | 0% | 0% | 0% | 0.005708% | 0.005708%
30 | 20 | 0% | 0 | 0.02283% | 4 | 0.02283% | 0.02283% | 0.02283% | 0.02283% | 0% | 0% | 0% | 0% | 0.02283% | 0.02283%
30 | 21 | 0% | 0 | 0.01142% | 2 | 0.01142% | 0.01142% | 0.01142% | 0.01142% | 0.01713% | 0.01713% | 0.01713% | 0.01713% | 0.01142% | 0.01142%
30 | 22 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
30 | 23 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
30 | 24 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
30 | 25 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
30 | 26 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
30 | 27 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
30 | 28 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
30 | 29 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
30 | 30 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
30 | 31 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
30 | 32 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
30 | 33 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
30 | 34 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
30 | 35 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
30 | 36 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
30 | 37 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
30 | 38 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
30 | 39 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
30 | 40 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
60 | 0 | 0.005709% | 1 | 0% | 0 | 0% | 0% | 0% | 0% | 0.005709% | 0.005709% | 0.005709% | 0.005709% | 0% | 0%
60 | 1 | 0.07993% | 14 | 0.06849% | 12 | 0.06849% | 0.06849% | 0.06849% | 0.06849% | 0.07993% | 0.07993% | 0.07993% | 0.07993% | 0.06849% | 0.06849%
60 | 2 | 0.2112% | 37 | 0.2169% | 38 | 0.1998% | 0.2169% | 0.2169% | 0.2169% | 0.2112% | 0.2112% | 0.2112% | 0.2112% | 0.1998% | 0.2169%
60 | 3 | 0.451% | 79 | 0.3539% | 62 | 0.371% | 0.3539% | 0.3539% | 0.3539% | 0.451% | 0.4282% | 0.451% | 0.451% | 0.371% | 0.3539%
60 | 4 | 0.4567% | 80 | 0.4852% | 85 | 0.4852% | 0.4852% | 0.4852% | 0.4852% | 0.4567% | 0.4796% | 0.4567% | 0.4567% | 0.4852% | 0.4852%
60 | 5 | 0.5195% | 91 | 0.4909% | 86 | 0.4909% | 0.4909% | 0.4909% | 0.4909% | 0.5138% | 0.5081% | 0.5195% | 0.5195% | 0.4909% | 0.4909%
60 | 6 | 0.4853% | 85 | 0.4509% | 79 | 0.4509% | 0.4509% | 0.4509% | 0.4509% | 0.491% | 0.4967% | 0.4853% | 0.4853% | 0.4509% | 0.4509%
60 | 7 | 0.4339% | 76 | 0.4566% | 80 | 0.4566% | 0.4566% | 0.4566% | 0.4566% | 0.4339% | 0.4339% | 0.4339% | 0.4339% | 0.4566% | 0.4566%
60 | 8 | 0.3083% | 54 | 0.5365% | 94 | 0.4852% | 0.4852% | 0.5308% | 0.4852% | 0.3083% | 0.3083% | 0.3083% | 0.3083% | 0.4852% | 0.5308%
60 | 9 | 0.3083% | 54 | 0.3539% | 62 | 0.4053% | 0.4053% | 0.3596% | 0.4053% | 0.3083% | 0.3083% | 0.3083% | 0.3083% | 0.4053% | 0.3596%
60 | 10 | 0.2341% | 41 | 0.2055% | 36 | 0.2055% | 0.2055% | 0.2055% | 0.2055% | 0.2341% | 0.2169% | 0.2341% | 0.2341% | 0.2055% | 0.2055%
60 | 11 | 0.1541% | 27 | 0.1712% | 30 | 0.1712% | 0.1712% | 0.1712% | 0.1712% | 0.1541% | 0.1713% | 0.1541% | 0.1541% | 0.1712% | 0.1712%
60 | 12 | 0.1028% | 18 | 0.1598% | 28 | 0.1541% | 0.1598% | 0.1598% | 0.1598% | 0.1028% | 0.1028% | 0.1028% | 0.1028% | 0.1541% | 0.1598%
60 | 13 | 0.06851% | 12 | 0.0742% | 13 | 0.06849% | 0.0742% | 0.0742% | 0.0742% | 0.06851% | 0.06851% | 0.06851% | 0.06851% | 0.06849% | 0.0742%
60 | 14 | 0.03996% | 7 | 0.07991% | 14 | 0.08562% | 0.0742% | 0.07991% | 0.0742% | 0.03996% | 0.03996% | 0.03996% | 0.03996% | 0.08562% | 0.07991%
60 | 15 | 0.02855% | 5 | 0.05137% | 9 | 0.05708% | 0.05708% | 0.05137% | 0.05708% | 0.02855% | 0.02855% | 0.02855% | 0.02855% | 0.05708% | 0.05137%
60 | 16 | 0.02284% | 4 | 0.03995% | 7 | 0.03995% | 0.03995% | 0.03995% | 0.03995% | 0.02284% | 0.02284% | 0.02284% | 0.02284% | 0.03995% | 0.03995%
60 | 17 | 0% | 0 | 0.01712% | 3 | 0.01712% | 0.01712% | 0.01712% | 0.01712% | 0% | 0% | 0% | 0% | 0.01712% | 0.01712%
60 | 18 | 0% | 0 | 0.02283% | 4 | 0.02283% | 0.02283% | 0.02283% | 0.02283% | 0% | 0% | 0% | 0% | 0.02283% | 0.02283%
60 | 19 | 0% | 0 | 0.005708% | 1 | bar: Wind Turbine 97 to Wind Turbine 108
60 | 20 | 0% | 0 | 0% | 0 | 0.005708% | 0.005708% | 0.005708% | 0.005708% | 0% | 0% | 0% | 0% | 0.005708% | 0.005708%
60 | 21 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
60 | 22 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
60 | 23 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
60 | 24 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
60 | 25 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
60 | 26 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
60 | 27 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
60 | 28 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
60 | 29 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
60 | 30 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
60 | 31 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
60 | 32 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
60 | 33 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
60 | 34 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
60 | 35 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
60 | 36 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
60 | 37 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
60 | 38 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
60 | 39 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
60 | 40 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
90 | 0 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
90 | 1 | 0.03425% | 6 | 0.0742% | 13 | 0.0742% | 0.0742% | 0.0742% | 0.0742% | 0.03425% | 0.03425% | 0.03425% | 0.03425% | 0.0742% | 0.0742%
90 | 2 | 0.1541% | 27 | 0.1313% | 23 | 0.1256% | 0.1313% | 0.1313% | 0.1313% | 0.1541% | 0.1541% | 0.1541% | 0.1541% | 0.1256% | 0.1313%
90 | 3 | 0.3368% | 59 | 0.2854% | 50 | 0.2854% | 0.2854% | 0.2854% | 0.2854% | 0.3368% | 0.2969% | 0.3368% | 0.3368% | 0.2854% | 0.2854%
90 | 4 | 0.491% | 86 | 0.3482% | 61 | 0.3539% | 0.3482% | 0.3482% | 0.3482% | 0.491% | 0.5309% | 0.491% | 0.491% | 0.3539% | 0.3482%
90 | 5 | 0.4624% | 81 | 0.4053% | 71 | 0.3995% | 0.4053% | 0.4053% | 0.4053% | 0.4624% | 0.4624% | 0.4624% | 0.4624% | 0.3995% | 0.4053%
90 | 6 | 0.3825% | 67 | 0.4966% | 87 | 0.5023% | 0.4966% | 0.4966% | 0.4966% | 0.3825% | 0.3825% | 0.3825% | 0.3825% | 0.5023% | 0.4966%
90 | 7 | 0.5481% | 96 | 0.4737% | 83 | 0.4737% | 0.4737% | 0.4737% | 0.4737% | 0.5481% | 0.5481% | 0.5481% | 0.5481% | 0.4737% | 0.4737%
90 | 8 | 0.4567% | 80 | 0.3938% | 69 | 0.3767% | 0.3767% | 0.3881% | 0.3767% | 0.4567% | 0.4567% | 0.4567% | 0.4567% | 0.3767% | 0.3881%
90 | 9 | 0.3597% | 63 | 0.2797% | 49 | 0.2968% | 0.2968% | 0.2854% | 0.2968% | 0.3597% | 0.3597% | 0.3597% | 0.3597% | 0.2968% | 0.2854%
90 | 10 | 0.3654% | 64 | 0.3025% | 53 | 0.3025% | 0.3025% | 0.3025% | 0.3025% | 0.3654% | 0.314% | 0.3654% | 0.3654% | 0.3025% | 0.3025%
90 | 11 | 0.1599% | 28 | 0.1884% | 33 | 0.1884% | 0.1884% | 0.1884% | 0.1884% | 0.1599% | 0.2112% | 0.1599% | 0.1599% | 0.1884% | 0.1884%
90 | 12 | 0.1713% | 30 | 0.1655% | 29 | 0.1655% | 0.1655% | 0.1655% | 0.1655% | 0.1713% | 0.1713% | 0.1713% | 0.1713% | 0.1655% | 0.1655%
90 | 13 | 0.04567% | 8 | 0.06849% | 12 | 0.06279% | 0.06849% | 0.06849% | 0.06849% | 0.04567% | 0.04567% | 0.04567% | 0.04567% | 0.06279% | 0.06849%
90 | 14 | 0.03996% | 7 | 0.05137% | 9 | 0.05708% | 0.05137% | 0.05137% | 0.05137% | 0.03996% | 0.03996% | 0.03996% | 0.03996% | 0.05708% | 0.05137%
90 | 15 | 0.005709% | 1 | 0.005708% | 1 | 0.005708% | 0.005708% | 0.005708% | 0.005708% | 0% | 0% | 0% | 0% | 0.005708% | 0.005708%
90 | 16 | 0% | 0 | 0.005708% | 1 | 0% | 0% | 0% | 0% | 0.005709% | 0.005709% | 0.005709% | 0.005709% | 0% | 0%
90 | 17 | 0% | 0 | 0.005708% | 1 | 0.005708% | 0.005708% | 0.005708% | 0.005708% | 0% | 0% | 0% | 0% | 0.005708% | 0.005708%
90 | 18 | 0% | 0 | 0.01142% | 2 | 0.005708% | 0.005708% | 0.005708% | 0.005708% | 0% | 0% | 0% | 0% | 0.005708% | 0.005708%
90 | 19 | 0% | 0 | 0.005708% | 1 | bar: Wind Turbine 97 to Wind Turbine 108
90 | 20 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
90 | 21 | 0% | 0 | 0% | 0 | 0.01142% | 0.01142% | 0.01142% | 0.01142% | 0% | 0% | 0% | 0% | 0.01142% | 0.01142%
90 | 22 | 0% | 0 | 0% | 0 | 0.005708% | 0.005708% | 0.005708% | 0.005708% | 0% | 0% | 0% | 0% | 0.005708% | 0.005708%
90 | 23 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
90 | 24 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
90 | 25 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
90 | 26 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
90 | 27 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
90 | 28 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
90 | 29 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
90 | 30 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
90 | 31 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
90 | 32 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
90 | 33 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
90 | 34 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
90 | 35 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
90 | 36 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
90 | 37 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
90 | 38 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
90 | 39 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
90 | 40 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
120 | 0 | 0% | 0 | 0.01142% | 2 | 0.01142% | 0.01142% | 0.01142% | 0.01142% | 0% | 0% | 0% | 0% | 0.01142% | 0.01142%
120 | 1 | 0.04567% | 8 | 0.05137% | 9 | 0.04566% | 0.05137% | 0.05137% | 0.05137% | 0.04567% | 0.04567% | 0.04567% | 0.04567% | 0.04566% | 0.05137%
120 | 2 | 0.2398% | 42 | 0.1484% | 26 | 0.137% | 0.1484% | 0.1484% | 0.1484% | 0.2398% | 0.2398% | 0.2398% | 0.2398% | 0.137% | 0.1484%
120 | 3 | 0.4396% | 77 | 0.3253% | 57 | 0.3425% | 0.3253% | 0.3253% | 0.3253% | 0.4396% | 0.3996% | 0.4396% | 0.4396% | 0.3425% | 0.3253%
120 | 4 | 0.5424% | 95 | 0.5194% | 91 | 0.5194% | 0.5194% | 0.5194% | 0.5194% | 0.5367% | 0.5766% | 0.5424% | 0.5424% | 0.5194% | 0.5194%
120 | 5 | 0.9077% | 159 | 0.6564% | 115 | 0.6564% | 0.6564% | 0.6564% | 0.6564% | 0.9135% | 0.9135% | 0.9077% | 0.9077% | 0.6564% | 0.6564%
120 | 6 | 0.6851% | 120 | 0.7648% | 134 | 0.7591% | 0.7591% | 0.7591% | 0.7591% | 0.6851% | 0.6851% | 0.6851% | 0.6851% | 0.7591% | 0.7591%
120 | 7 | 0.7764% | 136 | 0.6735% | 118 | 0.6792% | 0.6792% | 0.6792% | 0.6792% | 0.7764% | 0.7764% | 0.7764% | 0.7764% | 0.6792% | 0.6792%
120 | 8 | 0.8621% | 151 | 0.7705% | 135 | 0.7363% | 0.7363% | 0.7591% | 0.7363% | 0.8621% | 0.8621% | 0.8621% | 0.8621% | 0.7363% | 0.7591%
120 | 9 | 1.028% | 180 | 0.7135% | 125 | 0.7363% | 0.7363% | 0.7192% | 0.7363% | 1.028% | 1.028% | 1.028% | 1.028% | 0.7363% | 0.7192%
120 | 10 | 0.8621% | 151 | 0.645% | 113 | 0.6507% | 0.6564% | 0.6507% | 0.6564% | 0.8621% | 0.7536% | 0.8621% | 0.8621% | 0.6507% | 0.6507%
120 | 11 | 0.6623% | 116 | 0.5251% | 92 | 0.5308% | 0.5251% | 0.5251% | 0.5251% | 0.6623% | 0.7707% | 0.6623% | 0.6623% | 0.5308% | 0.5251%
120 | 12 | 0.3939% | 69 | 0.4509% | 79 | 0.4395% | 0.4452% | 0.4452% | 0.4452% | 0.3939% | 0.3939% | 0.3939% | 0.3939% | 0.4395% | 0.4452%
120 | 13 | 0.314% | 55 | 0.2283% | 40 | 0.234% | 0.2283% | 0.234% | 0.2283% | 0.314% | 0.314% | 0.314% | 0.314% | 0.234% | 0.234%
120 | 14 | 0.2455% | 43 | 0.2169% | 38 | 0.2055% | 0.2055% | 0.2169% | 0.2055% | 0.2455% | 0.2455% | 0.2455% | 0.2455% | 0.2055% | 0.2169%
120 | 15 | 0.09705% | 17 | 0.1142% | 20 | 0.1084% | 0.1084% | 0.09132% | 0.1084% | 0.09705% | 0.09705% | 0.09705% | 0.09705% | 0.1084% | 0.09132%
120 | 16 | 0.05138% | 9 | 0.09703% | 17 | 0.1199% | 0.1199% | 0.1199% | 0.1199% | 0.05138% | 0.05138% | 0.05138% | 0.05138% | 0.1199% | 0.1199%
120 | 17 | 0.03425% | 6 | 0.03425% | 6 | 0.02854% | 0.03425% | 0.03425% | 0.03425% | 0.03425% | 0.03425% | 0.03425% | 0.03425% | 0.02854% | 0.03425%
120 | 18 | 0.01142% | 2 | 0.02283% | 4 | 0.02854% | 0.02283% | 0.02283% | 0.02283% | 0.01142% | 0.01142% | 0.01142% | 0.01142% | 0.02854% | 0.02283%
120 | 19 | 0.005709% | 1 | 0% | 0 | 0% | 0% | 0% | 0% | 0.005709% | 0.005709% | 0.005709% | 0.005709% | 0% | 0%
120 | 20 | 0.01142% | 2 | 0% | 0 | 0% | 0% | 0% | 0% | 0.01142% | 0.01142% | 0.01142% | 0.01142% | 0% | 0%
120 | 21 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
120 | 22 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
120 | 23 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
120 | 24 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
120 | 25 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
120 | 26 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
120 | 27 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
120 | 28 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
120 | 29 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
120 | 30 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
120 | 31 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
120 | 32 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
120 | 33 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
120 | 34 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
120 | 35 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
120 | 36 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
120 | 37 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
120 | 38 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
120 | 39 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
120 | 40 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
150 | 0 | 0% | 0 | 0.005708% | 1 | 0.005708% | 0.005708% | 0.005708% | 0.005708% | 0% | 0% | 0% | 0% | 0.005708% | 0.005708%
150 | 1 | 0.06851% | 12 | 0.09703% | 17 | 0.09703% | 0.09703% | 0.09703% | 0.09703% | 0.06851% | 0.06851% | 0.06851% | 0.06851% | 0.09703% | 0.09703%
150 | 2 | 0.2626% | 46 | 0.2169% | 38 | 0.1941% | 0.2169% | 0.2169% | 0.2169% | 0.2626% | 0.2626% | 0.2626% | 0.2626% | 0.1941% | 0.2169%
150 | 3 | 0.3597% | 63 | 0.4053% | 71 | 0.4281% | 0.4053% | 0.4053% | 0.4053% | 0.3597% | 0.3254% | 0.3597% | 0.3597% | 0.4281% | 0.4053%
150 | 4 | 0.5024% | 88 | 0.6336% | 111 | 0.6336% | 0.6336% | 0.6336% | 0.6336% | 0.5024% | 0.5367% | 0.5024% | 0.5024% | 0.6336% | 0.6336%
150 | 5 | 0.7422% | 130 | 0.7306% | 128 | 0.7249% | 0.7249% | 0.7249% | 0.7249% | 0.7422% | 0.7422% | 0.7422% | 0.7422% | 0.7249% | 0.7249%
150 | 6 | 0.7193% | 126 | 0.8847% | 155 | 0.8904% | 0.8904% | 0.8904% | 0.8904% | 0.7193% | 0.7079% | 0.7193% | 0.7193% | 0.8904% | 0.8904%
150 | 7 | 1.159% | 203 | 1.09% | 191 | 1.09% | 1.09% | 1.09% | 1.09% | 1.159% | 1.17% | 1.159% | 1.159% | 1.09% | 1.09%
150 | 8 | 1.376% | 241 | 1.067% | 187 | 0.9989% | 0.9989% | 1.067% | 0.9989% | 1.376% | 1.376% | 1.376% | 1.376% | 0.9989% | 1.067%
150 | 9 | 1.656% | 290 | 1.159% | 203 | 1.227% | 1.227% | 1.159% | 1.227% | 1.656% | 1.656% | 1.656% | 1.656% | 1.227% | 1.159%
150 | 10 | 1.633% | 286 | 1.164% | 204 | 1.147% | 1.159% | 1.164% | 1.159% | 1.633% | 1.49% | 1.633% | 1.633% | 1.147% | 1.164%
150 | 11 | 0.8792% | 154 | 1.022% | 179 | 1.039% | 1.027% | 1.022% | 1.027% | 0.8792% | 1.022% | 0.8792% | 0.8792% | 1.039% | 1.022%
150 | 12 | 0.942% | 165 | 0.7705% | 135 | 0.7705% | 0.7705% | 0.7705% | 0.7705% | 0.942% | 0.942% | 0.942% | 0.942% | 0.7705% | 0.7705%
150 | 13 | 0.805% | 141 | 0.7021% | 123 | 0.6393% | 0.6963% | 0.7021% | 0.6963% | 0.805% | 0.7993% | 0.805% | 0.805% | 0.6393% | 0.7021%
150 | 14 | 0.6965% | 122 | 0.6849% | 120 | 0.7021% | 0.6507% | 0.6849% | 0.6507% | 0.6965% | 0.7022% | 0.6965% | 0.6965% | 0.7021% | 0.6849%
150 | 15 | 0.3825% | 67 | 0.4566% | 80 | 0.4452% | 0.4566% | 0.4167% | 0.4566% | 0.3368% | 0.3368% | 0.3825% | 0.3825% | 0.4452% | 0.4167%
150 | 16 | 0.1713% | 30 | 0.1884% | 33 | 0.2397% | 0.2226% | 0.2226% | 0.2226% | 0.2169% | 0.2169% | 0.1713% | 0.1713% | 0.2397% | 0.2226%
150 | 17 | 0.1656% | 29 | 0.1598% | 28 | 0.1598% | 0.1655% | 0.1655% | 0.1655% | 0.1599% | 0.1313% | 0.1656% | 0.1656% | 0.1598% | 0.1655%
150 | 18 | 0.06851% | 12 | 0.07991% | 14 | 0.07991% | 0.0742% | 0.07991% | 0.0742% | 0.07422% | 0.1028% | 0.06851% | 0.06851% | 0.07991% | 0.07991%
150 | 19 | 0.0628% | 11 | 0.03995% | 7 | 0.04566% | 0.04566% | 0.03995% | 0.04566% | 0.0628% | 0.05709% | 0.0628% | 0.0628% | 0.04566% | 0.03995%
150 | 20 | 0.02284% | 4 | 0.02283% | 4 | 0.02283% | 0.02283% | 0.02283% | 0.02283% | 0.02284% | 0.02855% | 0.02284% | 0.02284% | 0.02283% | 0.02283%
150 | 21 | 0.03996% | 7 | 0.01712% | 3 | 0.01712% | 0.01712% | 0.01712% | 0.01712% | 0.03996% | 0.03996% | 0.03996% | 0.03996% | 0.01712% | 0.01712%
150 | 22 | 0.02284% | 4 | 0.005708% | 1 | 0.005708% | 0.005708% | 0.005708% | 0.005708% | 0.01713% | 0.01713% | 0.02284% | 0.02284% | 0.005708% | 0.005708%
150 | 23 | 0% | 0 | 0.01142% | 2 | 0.01142% | 0.01142% | 0.01142% | 0.01142% | 0.005709% | 0.005709% | 0% | 0% | 0.01142% | 0.01142%
150 | 24 | 0% | 0 | 0.005708% | 1 | bar: Wind Turbine 97 to Wind Turbine 108
150 | 25 | 0% | 0 | 0% | 0 | 0.005708% | 0.005708% | 0.005708% | 0.005708% | 0% | 0% | 0% | 0% | 0.005708% | 0.005708%
150 | 26 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
150 | 27 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
150 | 28 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
150 | 29 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
150 | 30 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
150 | 31 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
150 | 32 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
150 | 33 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
150 | 34 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
150 | 35 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
150 | 36 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
150 | 37 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
150 | 38 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
150 | 39 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
150 | 40 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
180 | 0 | 0.005709% | 1 | 0% | 0 | 0% | 0% | 0% | 0% | 0.005709% | 0.005709% | 0.005709% | 0.005709% | 0% | 0%
180 | 1 | 0.1085% | 19 | 0.1427% | 25 | 0.1427% | 0.1427% | 0.1427% | 0.1427% | 0.1085% | 0.1085% | 0.1085% | 0.1085% | 0.1427% | 0.1427%
180 | 2 | 0.2569% | 45 | 0.3025% | 53 | 0.2797% | 0.3025% | 0.3025% | 0.3025% | 0.2569% | 0.2569% | 0.2569% | 0.2569% | 0.2797% | 0.3025%
180 | 3 | 0.3311% | 58 | 0.4737% | 83 | 0.4966% | 0.4737% | 0.4737% | 0.4737% | 0.3311% | 0.3083% | 0.3311% | 0.3311% | 0.4966% | 0.4737%
180 | 4 | 0.4339% | 76 | 0.4909% | 86 | 0.4909% | 0.4909% | 0.4909% | 0.4909% | 0.4339% | 0.4567% | 0.4339% | 0.4339% | 0.4909% | 0.4909%
180 | 5 | 0.7022% | 123 | 0.6393% | 112 | 0.6336% | 0.6393% | 0.6393% | 0.6393% | 0.7022% | 0.7022% | 0.7022% | 0.7022% | 0.6336% | 0.6393%
180 | 6 | 0.8735% | 153 | 0.8505% | 149 | 0.8447% | 0.839% | 0.8447% | 0.839% | 0.8735% | 0.8678% | 0.8735% | 0.8735% | 0.8447% | 0.8447%
180 | 7 | 1.09% | 191 | 1.119% | 196 | 1.113% | 1.113% | 1.119% | 1.113% | 1.09% | 1.096% | 1.09% | 1.09% | 1.113% | 1.119%
180 | 8 | 1.336% | 234 | 0.9989% | 175 | 0.9189% | 0.9361% | 0.9932% | 0.9361% | 1.33% | 1.33% | 1.336% | 1.336% | 0.9189% | 0.9932%
180 | 9 | 1.604% | 281 | 1.204% | 211 | 1.29% | 1.279% | 1.21% | 1.279% | 1.61% | 1.61% | 1.604% | 1.604% | 1.29% | 1.21%
180 | 10 | 1.621% | 284 | 1.336% | 234 | 1.313% | 1.33% | 1.341% | 1.33% | 1.621% | 1.456% | 1.621% | 1.621% | 1.313% | 1.341%
180 | 11 | 1.159% | 203 | 1.387% | 243 | 1.421% | 1.398% | 1.387% | 1.398% | 1.159% | 1.325% | 1.159% | 1.159% | 1.421% | 1.387%
180 | 12 | 1.227% | 215 | 1.341% | 235 | 1.336% | 1.341% | 1.341% | 1.341% | 1.227% | 1.227% | 1.227% | 1.227% | 1.336% | 1.341%
180 | 13 | 0.6508% | 114 | 1.136% | 199 | 1.09% | 1.13% | 1.136% | 1.13% | 0.6508% | 0.6451% | 0.6508% | 0.6508% | 1.09% | 1.136%
180 | 14 | 0.6109% | 107 | 1.056% | 185 | 0.9646% | 0.9304% | 1.056% | 0.9304% | 0.6109% | 0.6166% | 0.6109% | 0.6109% | 0.9646% | 1.056%
180 | 15 | 0.4396% | 77 | 0.5936% | 104 | 0.6621% | 0.6507% | 0.5251% | 0.6507% | 0.3882% | 0.3882% | 0.4396% | 0.4396% | 0.6621% | 0.5251%
180 | 16 | 0.274% | 48 | 0.3311% | 58 | 0.3995% | 0.4053% | 0.3995% | 0.4053% | 0.3254% | 0.3254% | 0.274% | 0.274% | 0.3995% | 0.3995%
180 | 17 | 0.2626% | 46 | 0.2454% | 43 | 0.2283% | 0.2454% | 0.2454% | 0.2454% | 0.2626% | 0.2341% | 0.2626% | 0.2626% | 0.2283% | 0.2454%
180 | 18 | 0.1484% | 26 | 0.2169% | 38 | 0.2397% | 0.2169% | 0.2169% | 0.2169% | 0.1484% | 0.177% | 0.1484% | 0.1484% | 0.2397% | 0.2169%
180 | 19 | 0.1484% | 26 | 0.09132% | 16 | 0.0742% | 0.0742% | 0.09132% | 0.0742% | 0.1484% | 0.1427% | 0.1484% | 0.1484% | 0.0742% | 0.09132%
180 | 20 | 0.07422% | 13 | 0.06279% | 11 | 0.07991% | 0.07991% | 0.06279% | 0.07991% | 0.07422% | 0.07993% | 0.07422% | 0.07422% | 0.07991% | 0.06279%
180 | 21 | 0.0628% | 11 | 0.06849% | 12 | 0.05137% | 0.05137% | 0.05137% | 0.05137% | 0.0628% | 0.0628% | 0.0628% | 0.0628% | 0.05137% | 0.05137%
180 | 22 | 0.02855% | 5 | 0.05708% | 10 | 0.0742% | 0.0742% | 0.0742% | 0.0742% | 0.02284% | 0.02284% | 0.02855% | 0.02855% | 0.0742% | 0.0742%
180 | 23 | 0.02284% | 4 | 0.01712% | 3 | 0.01142% | 0.01712% | 0.01712% | 0.01712% | 0.02855% | 0.02855% | 0.02284% | 0.02284% | 0.01142% | 0.01712%
180 | 24 | 0.02855% | 5 | 0.005708% | 1 | 0.01142% | 0.005708% | 0.005708% | 0.005708% | 0.02855% | 0.02284% | 0.02855% | 0.02855% | 0.01142% | 0.005708%
180 | 25 | 0.01142% | 2 | 0.01142% | 2 | 0.01142% | 0.01142% | 0.01142% | 0.01142% | 0.01142% | 0.01713% | 0.01142% | 0.01142% | 0.01142% | 0.01142%
180 | 26 | 0.005709% | 1 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
180 | 27 | 0.005709% | 1 | 0% | 0 | 0% | 0% | 0% | 0% | 0.005709% | 0.005709% | 0.005709% | 0.005709% | 0% | 0%
180 | 28 | 0% | 0 | 0% | 0 | 0% | 0% | 0% | 0% | 0.005709% | 0.005709% | 0.005709% | 0.005709% | 0% | 0%
180 | 29 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
180 | 30 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
180 | 31 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
180 | 32 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
180 | 33 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
180 | 34 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
180 | 35 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
180 | 36 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
180 | 37 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
180 | 38 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
180 | 39 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
180 | 40 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
210 | 0 | 0.005709% | 1 | 0.005708% | 1 | 0.005708% | 0.005708% | 0.005708% | 0.005708% | 0.005709% | 0.005709% | 0.005709% | 0.005709% | 0.005708% | 0.005708%
210 | 1 | 0.09705% | 17 | 0.05708% | 10 | 0.05708% | 0.05708% | 0.05708% | 0.05708% | 0.09705% | 0.09705% | 0.09705% | 0.09705% | 0.05708% | 0.05708%
210 | 2 | 0.2284% | 40 | 0.1769% | 31 | 0.1598% | 0.1769% | 0.1769% | 0.1769% | 0.2284% | 0.2284% | 0.2284% | 0.2284% | 0.1598% | 0.1769%
210 | 3 | 0.4111% | 72 | 0.3539% | 62 | 0.3653% | 0.3482% | 0.3539% | 0.3482% | 0.4111% | 0.3882% | 0.4111% | 0.4111% | 0.3653% | 0.3539%
210 | 4 | 0.3939% | 69 | 0.4224% | 74 | 0.4281% | 0.4281% | 0.4224% | 0.4281% | 0.3939% | 0.4168% | 0.3939% | 0.3939% | 0.4281% | 0.4224%
210 | 5 | 0.5709% | 100 | 0.411% | 72 | 0.411% | 0.411% | 0.411% | 0.411% | 0.5709% | 0.5709% | 0.5709% | 0.5709% | 0.411% | 0.411%
210 | 6 | 0.628% | 110 | 0.4623% | 81 | 0.4623% | 0.4623% | 0.4623% | 0.4623% | 0.628% | 0.6223% | 0.628% | 0.628% | 0.4623% | 0.4623%
210 | 7 | 1.056% | 185 | 0.6336% | 111 | 0.6279% | 0.6336% | 0.6336% | 0.6336% | 1.056% | 1.062% | 1.056% | 1.056% | 0.6279% | 0.6336%
210 | 8 | 1.056% | 185 | 0.645% | 113 | 0.5708% | 0.5651% | 0.645% | 0.5651% | 1.045% | 1.045% | 1.056% | 1.056% | 0.5708% | 0.645%
210 | 9 | 1.245% | 218 | 0.5422% | 95 | 0.6164% | 0.6164% | 0.5422% | 0.6164% | 1.256% | 1.256% | 1.245% | 1.245% | 0.6164% | 0.5422%
210 | 10 | 1.273% | 223 | 0.5822% | 102 | 0.5765% | 0.5822% | 0.5822% | 0.5822% | 1.273% | 1.136% | 1.273% | 1.273% | 0.5765% | 0.5822%
210 | 11 | 0.7422% | 130 | 0.7021% | 123 | 0.7078% | 0.7021% | 0.6963% | 0.7021% | 0.7422% | 0.8792% | 0.7422% | 0.7422% | 0.7078% | 0.6963%
210 | 12 | 0.5309% | 93 | 0.7192% | 126 | 0.7192% | 0.7249% | 0.7249% | 0.7249% | 0.5309% | 0.5309% | 0.5309% | 0.5309% | 0.7192% | 0.7249%
210 | 13 | 0.2797% | 49 | 0.8276% | 145 | 0.7648% | 0.8219% | 0.8276% | 0.8219% | 0.2797% | 0.2797% | 0.2797% | 0.2797% | 0.7648% | 0.8276%
210 | 14 | 0.1884% | 33 | 0.5765% | 101 | 0.605% | 0.5422% | 0.5765% | 0.5422% | 0.1884% | 0.1884% | 0.1884% | 0.1884% | 0.605% | 0.5765%
210 | 15 | 0.1028% | 18 | 0.3539% | 62 | 0.3539% | 0.3539% | 0.3139% | 0.3539% | 0.1028% | 0.1028% | 0.1028% | 0.1028% | 0.3539% | 0.3139%
210 | 16 | 0.03996% | 7 | 0.1712% | 30 | 0.2055% | 0.2055% | 0.2055% | 0.2055% | 0.03996% | 0.03996% | 0.03996% | 0.03996% | 0.2055% | 0.2055%
210 | 17 | 0.02855% | 5 | 0.05137% | 9 | 0.03995% | 0.05708% | 0.05708% | 0.05708% | 0.02855% | 0.02284% | 0.02855% | 0.02855% | 0.03995% | 0.05708%
210 | 18 | 0.05138% | 9 | 0.05708% | 10 | 0.06849% | 0.05708% | 0.05708% | 0.05708% | 0.05138% | 0.05709% | 0.05138% | 0.05138% | 0.06849% | 0.05708%
210 | 19 | 0.005709% | 1 | 0.01142% | 2 | 0.01712% | 0.01142% | 0.01142% | 0.01142% | 0.005709% | 0.005709% | 0.005709% | 0.005709% | 0.01712% | 0.01142%
210 | 20 | 0.01142% | 2 | 0.02854% | 5 | 0.02854% | 0.02854% | 0.02854% | 0.02854% | 0.01142% | 0.01142% | 0.01142% | 0.01142% | 0.02854% | 0.02854%
210 | 21 | 0.01713% | 3 | 0.005708% | 1 | 0% | 0% | 0% | 0% | 0.01713% | 0.01713% | 0.01713% | 0.01713% | 0% | 0%
210 | 22 | 0% | 0 | 0.005708% | 1 | 0.005708% | 0.005708% | 0.005708% | 0.005708% | 0% | 0% | 0% | 0% | 0.005708% | 0.005708%
210 | 23 | 0% | 0 | 0% | 0 | 0.005708% | 0.005708% | 0.005708% | 0.005708% | 0% | 0% | 0% | 0% | 0.005708% | 0.005708%
210 | 24 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
210 | 25 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
210 | 26 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
210 | 27 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
210 | 28 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
210 | 29 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
210 | 30 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
210 | 31 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
210 | 32 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
210 | 33 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
210 | 34 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
210 | 35 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
210 | 36 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
210 | 37 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
210 | 38 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
210 | 39 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
210 | 40 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
240 | 0 | 0.005709% | 1 | 0.01142% | 2 | 0.01142% | 0.01142% | 0.01142% | 0.01142% | 0.005709% | 0.005709% | 0.005709% | 0.005709% | 0.01142% | 0.01142%
240 | 1 | 0.06851% | 12 | 0.0742% | 13 | 0.0742% | 0.0742% | 0.0742% | 0.0742% | 0.06851% | 0.06851% | 0.06851% | 0.06851% | 0.0742% | 0.0742%
240 | 2 | 0.2227% | 39 | 0.274% | 48 | 0.234% | 0.274% | 0.274% | 0.274% | 0.2227% | 0.2227% | 0.2227% | 0.2227% | 0.234% | 0.274%
240 | 3 | 0.451% | 79 | 0.4566% | 80 | 0.4966% | 0.4566% | 0.4566% | 0.4566% | 0.451% | 0.4168% | 0.451% | 0.451% | 0.4966% | 0.4566%
240 | 4 | 0.4567% | 80 | 0.5308% | 93 | 0.5308% | 0.5308% | 0.5308% | 0.5308% | 0.4567% | 0.491% | 0.4567% | 0.4567% | 0.5308% | 0.5308%
240 | 5 | 0.6337% | 111 | 0.4338% | 76 | 0.4338% | 0.4338% | 0.4338% | 0.4338% | 0.6337% | 0.6337% | 0.6337% | 0.6337% | 0.4338% | 0.4338%
240 | 6 | 0.5937% | 104 | 0.5251% | 92 | 0.5194% | 0.5194% | 0.5194% | 0.5194% | 0.5937% | 0.5937% | 0.5937% | 0.5937% | 0.5194% | 0.5194%
240 | 7 | 0.7879% | 138 | 0.6906% | 121 | 0.6963% | 0.6963% | 0.6963% | 0.6963% | 0.7879% | 0.7879% | 0.7879% | 0.7879% | 0.6963% | 0.6963%
240 | 8 | 0.8849% | 155 | 0.5822% | 102 | 0.5422% | 0.5479% | 0.5822% | 0.5479% | 0.8849% | 0.8849% | 0.8849% | 0.8849% | 0.5422% | 0.5822%
240 | 9 | 0.8621% | 151 | 0.5422% | 95 | 0.5822% | 0.5765% | 0.5422% | 0.5765% | 0.8621% | 0.8621% | 0.8621% | 0.8621% | 0.5822% | 0.5422%
240 | 10 | 0.9705% | 170 | 0.605% | 106 | 0.5993% | 0.605% | 0.605% | 0.605% | 0.9705% | 0.8735% | 0.9705% | 0.9705% | 0.5993% | 0.605%
240 | 11 | 0.7079% | 124 | 0.5993% | 105 | 0.605% | 0.5993% | 0.5993% | 0.5993% | 0.7079% | 0.805% | 0.7079% | 0.7079% | 0.605% | 0.5993%
240 | 12 | 0.3939% | 69 | 0.6393% | 112 | 0.6393% | 0.6393% | 0.6393% | 0.6393% | 0.3939% | 0.3939% | 0.3939% | 0.3939% | 0.6393% | 0.6393%
240 | 13 | 0.2797% | 49 | 0.4566% | 80 | 0.4338% | 0.4566% | 0.4566% | 0.4566% | 0.2797% | 0.274% | 0.2797% | 0.2797% | 0.4338% | 0.4566%
240 | 14 | 0.1599% | 28 | 0.2797% | 49 | 0.3025% | 0.2797% | 0.2797% | 0.2797% | 0.1599% | 0.1656% | 0.1599% | 0.1599% | 0.3025% | 0.2797%
240 | 15 | 0.09135% | 16 | 0.1199% | 21 | 0.1142% | 0.1142% | 0.1142% | 0.1142% | 0.06851% | 0.06851% | 0.09135% | 0.09135% | 0.1142% | 0.1142%
240 | 16 | 0.08564% | 15 | 0.05708% | 10 | 0.06279% | 0.06279% | 0.06279% | 0.06279% | 0.1085% | 0.1085% | 0.08564% | 0.08564% | 0.06279% | 0.06279%
240 | 17 | 0.01713% | 3 | 0.02283% | 4 | 0.02283% | 0.02283% | 0.02283% | 0.02283% | 0.01713% | 0.01713% | 0.01713% | 0.01713% | 0.02283% | 0.02283%
240 | 18 | 0.005709% | 1 | 0.05708% | 10 | 0.05708% | 0.05708% | 0.05708% | 0.05708% | 0.005709% | 0.005709% | 0.005709% | 0.005709% | 0.05708% | 0.05708%
240 | 19 | 0.01713% | 3 | 0.06849% | 12 | 0.06849% | 0.06849% | 0.06849% | 0.06849% | 0.01713% | 0.01142% | 0.01713% | 0.01713% | 0.06849% | 0.06849%
240 | 20 | 0.02284% | 4 | 0.03995% | 7 | 0.03995% | 0.03995% | 0.03995% | 0.03995% | 0.02284% | 0.02855% | 0.02284% | 0.02284% | 0.03995% | 0.03995%
240 | 21 | 0.005709% | 1 | 0.01712% | 3 | 0.01142% | 0.01142% | 0.01142% | 0.01142% | 0.005709% | 0.005709% | 0.005709% | 0.005709% | 0.01142% | 0.01142%
240 | 22 | 0.01713% | 3 | 0.005708% | 1 | 0.01142% | 0.01142% | 0.01142% | 0.01142% | 0.01713% | 0.01713% | 0.01713% | 0.01713% | 0.01142% | 0.01142%
240 | 23 | 0.005709% | 1 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
240 | 24 | 0% | 0 | 0% | 0 | 0% | 0% | 0% | 0% | 0.005709% | 0.005709% | 0.005709% | 0.005709% | 0% | 0%
240 | 25 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
240 | 26 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
240 | 27 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
240 | 28 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
240 | 29 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
240 | 30 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
240 | 31 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
240 | 32 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
240 | 33 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
240 | 34 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
240 | 35 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
240 | 36 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
240 | 37 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
240 | 38 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
240 | 39 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
240 | 40 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
270 | 0 | 0.02284% | 4 | 0.08562% | 15 | 0% | 0% | 0% | 0% | 0.02284% | 0.02284% | 0.02284% | 0.02284% | 0% | 0%
270 | 1 | 0.06851% | 12 | 0.2454% | 43 | 0.08562% | 0.08562% | 0.08562% | 0.08562% | 0.06851% | 0.06851% | 0.06851% | 0.06851% | 0.08562% | 0.08562%
270 | 2 | 0.1541% | 27 | 0.5308% | 93 | 0.2169% | 0.2397% | 0.2397% | 0.2397% | 0.1541% | 0.1541% | 0.1541% | 0.1541% | 0.2169% | 0.2397%
270 | 3 | 0.2569% | 45 | 0.7705% | 135 | 0.5594% | 0.5365% | 0.5365% | 0.5365% | 0.2569% | 0.2512% | 0.2569% | 0.2569% | 0.5594% | 0.5365%
270 | 4 | 0.5538% | 97 | 0.8505% | 149 | 0.7705% | 0.7705% | 0.7705% | 0.7705% | 0.5538% | 0.5595% | 0.5538% | 0.5538% | 0.7705% | 0.7705%
270 | 5 | 0.5024% | 88 | 1.221% | 214 | 0.8505% | 0.8505% | 0.8505% | 0.8505% | 0.5024% | 0.5024% | 0.5024% | 0.5024% | 0.8505% | 0.8505%
270 | 6 | 0.8735% | 153 | 1.341% | 235 | 1.21% | 1.216% | 1.216% | 1.216% | 0.8735% | 0.8678% | 0.8735% | 0.8735% | 1.21% | 1.216%
270 | 7 | 0.8735% | 153 | 1.444% | 253 | 1.336% | 1.341% | 1.347% | 1.341% | 0.8735% | 0.8792% | 0.8735% | 0.8735% | 1.336% | 1.347%
270 | 8 | 0.902% | 158 | 1.513% | 265 | 1.336% | 1.324% | 1.438% | 1.324% | 0.8963% | 0.8963% | 0.902% | 0.902% | 1.336% | 1.438%
270 | 9 | 0.7993% | 140 | 1.296% | 227 | 1.615% | 1.627% | 1.518% | 1.627% | 0.805% | 0.805% | 0.7993% | 0.7993% | 1.615% | 1.518%
270 | 10 | 0.7821% | 137 | 0.8961% | 157 | 1.307% | 1.296% | 1.296% | 1.296% | 0.7821% | 0.7079% | 0.7821% | 0.7821% | 1.307% | 1.296%
270 | 11 | 0.6223% | 109 | 0.7021% | 123 | 0.8847% | 0.8961% | 0.8847% | 0.8961% | 0.6223% | 0.6965% | 0.6223% | 0.6223% | 0.8847% | 0.8847%
270 | 12 | 0.6223% | 109 | 0.5308% | 93 | 0.7249% | 0.7135% | 0.7135% | 0.7135% | 0.6223% | 0.6223% | 0.6223% | 0.6223% | 0.7249% | 0.7135%
270 | 13 | 0.4396% | 77 | 0.2626% | 46 | 0.508% | 0.5308% | 0.5308% | 0.5308% | 0.4396% | 0.4282% | 0.4396% | 0.4396% | 0.508% | 0.5308%
270 | 14 | 0.3654% | 64 | 0.1427% | 25 | 0.2454% | 0.2226% | 0.2626% | 0.2226% | 0.3654% | 0.3711% | 0.3654% | 0.3654% | 0.2454% | 0.2626%
270 | 15 | 0.2569% | 45 | 0.09132% | 16 | 0.1655% | 0.1655% | 0.1256% | 0.1655% | 0.2398% | 0.2455% | 0.2569% | 0.2569% | 0.1655% | 0.1256%
270 | 16 | 0.1199% | 21 | 0.06279% | 11 | 0.1084% | 0.1084% | 0.1084% | 0.1084% | 0.137% | 0.1313% | 0.1199% | 0.1199% | 0.1084% | 0.1084%
270 | 17 | 0.1256% | 22 | 0.04566% | 8 | 0.05708% | 0.06279% | 0.06279% | 0.06279% | 0.1256% | 0.1085% | 0.1256% | 0.1256% | 0.05708% | 0.06279%
270 | 18 | 0.02855% | 5 | 0.03995% | 7 | 0.05137% | 0.04566% | 0.04566% | 0.04566% | 0.02855% | 0.05138% | 0.02855% | 0.02855% | 0.05137% | 0.04566%
270 | 19 | 0.03425% | 6 | 0.08562% | 15 | 0.03995% | 0.03995% | 0.03995% | 0.03995% | 0.03425% | 0.03425% | 0.03425% | 0.03425% | 0.03995% | 0.03995%
270 | 20 | 0.005709% | 1 | 0.03425% | 6 | 0.07991% | 0.07991% | 0.08562% | 0.07991% | 0.005709% | 0.005709% | 0.005709% | 0.005709% | 0.07991% | 0.08562%
270 | 21 | 0.02855% | 5 | 0.01712% | 3 | 0.03995% | 0.03995% | 0.03425% | 0.03995% | 0.02855% | 0.02855% | 0.02855% | 0.02855% | 0.03995% | 0.03425%
270 | 22 | 0.005709% | 1 | 0.005708% | 1 | 0.01712% | 0.01712% | 0.01712% | 0.01712% | 0.005709% | 0.005709% | 0.005709% | 0.005709% | 0.01712% | 0.01712%
270 | 23 | 0.01142% | 2 | 0% | 0 | 0.005708% | 0.005708% | 0.005708% | 0.005708% | 0.01142% | 0.01142% | 0.01142% | 0.01142% | 0.005708% | 0.005708%
270 | 24 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
270 | 25 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
270 | 26 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
270 | 27 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
270 | 28 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
270 | 29 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
270 | 30 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
270 | 31 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
270 | 32 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
270 | 33 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
270 | 34 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
270 | 35 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
270 | 36 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
270 | 37 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
270 | 38 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
270 | 39 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
270 | 40 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
300 | 0 | 0.01142% | 2 | 0.005708% | 1 | 0.005708% | 0.005708% | 0.005708% | 0.005708% | 0.01142% | 0.01142% | 0.01142% | 0.01142% | 0.005708% | 0.005708%
300 | 1 | 0.08564% | 15 | 0.137% | 24 | 0.137% | 0.137% | 0.137% | 0.137% | 0.08564% | 0.08564% | 0.08564% | 0.08564% | 0.137% | 0.137%
300 | 2 | 0.2455% | 43 | 0.3881% | 68 | 0.3425% | 0.3881% | 0.3881% | 0.3881% | 0.2455% | 0.2398% | 0.2455% | 0.2455% | 0.3425% | 0.3881%
300 | 3 | 0.5424% | 95 | 0.4966% | 87 | 0.5422% | 0.4966% | 0.4966% | 0.4966% | 0.5424% | 0.5024% | 0.5424% | 0.5424% | 0.5422% | 0.4966%
300 | 4 | 0.7308% | 128 | 1.17% | 205 | 1.164% | 1.17% | 1.17% | 1.17% | 0.7251% | 0.7707% | 0.7308% | 0.7308% | 1.164% | 1.17%
300 | 5 | 0.9249% | 162 | 1.067% | 187 | 1.073% | 1.067% | 1.067% | 1.067% | 0.9306% | 0.9249% | 0.9249% | 0.9249% | 1.073% | 1.067%
300 | 6 | 0.8849% | 155 | 1.336% | 234 | 1.324% | 1.324% | 1.324% | 1.324% | 0.8849% | 0.8849% | 0.8849% | 0.8849% | 1.324% | 1.324%
300 | 7 | 1.085% | 190 | 1.336% | 234 | 1.347% | 1.347% | 1.347% | 1.347% | 1.085% | 1.09% | 1.085% | 1.085% | 1.347% | 1.347%
300 | 8 | 1.096% | 192 | 1.49% | 261 | 1.37% | 1.37% | 1.484% | 1.37% | 1.09% | 1.09% | 1.096% | 1.096% | 1.37% | 1.484%
300 | 9 | 1.159% | 203 | 1.233% | 216 | 1.347% | 1.353% | 1.239% | 1.353% | 1.165% | 1.165% | 1.159% | 1.159% | 1.347% | 1.239%
300 | 10 | 1.17% | 205 | 1.062% | 186 | 1.05% | 1.056% | 1.062% | 1.056% | 1.17% | 0.9991% | 1.17% | 1.17% | 1.05% | 1.062%
300 | 11 | 0.8564% | 150 | 0.8276% | 145 | 0.8447% | 0.8333% | 0.8276% | 0.8333% | 0.8564% | 1.028% | 0.8564% | 0.8564% | 0.8447% | 0.8276%
300 | 12 | 0.7193% | 126 | 0.5594% | 98 | 0.5537% | 0.5594% | 0.5594% | 0.5594% | 0.7193% | 0.7193% | 0.7193% | 0.7193% | 0.5537% | 0.5594%
300 | 13 | 0.5367% | 94 | 0.3368% | 59 | 0.3311% | 0.3368% | 0.3368% | 0.3368% | 0.5367% | 0.5367% | 0.5367% | 0.5367% | 0.3311% | 0.3368%
300 | 14 | 0.4453% | 78 | 0.2511% | 44 | 0.2283% | 0.2169% | 0.2511% | 0.2169% | 0.4453% | 0.4453% | 0.4453% | 0.4453% | 0.2283% | 0.2511%
300 | 15 | 0.177% | 31 | 0.1484% | 26 | 0.1655% | 0.1655% | 0.1313% | 0.1655% | 0.1713% | 0.1713% | 0.177% | 0.177% | 0.1655% | 0.1313%
300 | 16 | 0.1142% | 20 | 0.1084% | 19 | 0.1199% | 0.1256% | 0.1256% | 0.1256% | 0.1199% | 0.1199% | 0.1142% | 0.1142% | 0.1199% | 0.1256%
300 | 17 | 0.03996% | 7 | 0.04566% | 8 | 0.04566% | 0.04566% | 0.04566% | 0.04566% | 0.03996% | 0.03425% | 0.03996% | 0.03996% | 0.04566% | 0.04566%
300 | 18 | 0.03425% | 6 | 0.06279% | 11 | 0.06849% | 0.06279% | 0.06279% | 0.06279% | 0.03425% | 0.03996% | 0.03425% | 0.03425% | 0.06849% | 0.06279%
300 | 19 | 0.01713% | 3 | 0.04566% | 8 | 0.04566% | 0.04566% | 0.04566% | 0.04566% | 0.01713% | 0.01713% | 0.01713% | 0.01713% | 0.04566% | 0.04566%
300 | 20 | 0.03425% | 6 | 0.005708% | 1 | 0.005708% | 0.005708% | 0.005708% | 0.005708% | 0.03425% | 0.03425% | 0.03425% | 0.03425% | 0.005708% | 0.005708%
300 | 21 | 0.005709% | 1 | 0.01142% | 2 | 0.01142% | 0.01142% | 0.01142% | 0.01142% | 0.005709% | 0.005709% | 0.005709% | 0.005709% | 0.01142% | 0.01142%
300 | 22 | 0.02855% | 5 | 0.01142% | 2 | 0.01142% | 0.01142% | 0.01142% | 0.01142% | 0.02284% | 0.02284% | 0.02855% | 0.02855% | 0.01142% | 0.01142%
300 | 23 | 0.005709% | 1 | 0.005708% | 1 | 0.005708% | 0.005708% | 0.005708% | 0.005708% | 0.01142% | 0.01142% | 0.005709% | 0.005709% | 0.005708% | 0.005708%
300 | 24 | 0.005709% | 1 | 0.005708% | 1 | 0.005708% | 0.005708% | 0.005708% | 0.005708% | 0.005709% | 0.005709% | 0.005709% | 0.005709% | 0.005708% | 0.005708%
300 | 25 | 0% | 0 | 0.005708% | 1 | 0.005708% | 0.005708% | 0.005708% | 0.005708% | 0% | 0% | 0% | 0% | 0.005708% | 0.005708%
300 | 26 | 0% | 0 | 0.005708% | 1 | 0.005708% | 0.005708% | 0.005708% | 0.005708% | 0% | 0% | 0% | 0% | 0.005708% | 0.005708%
300 | 27 | 0% | 0 | 0.005708% | 1 | 0.005708% | 0.005708% | 0.005708% | 0.005708% | 0% | 0% | 0% | 0% | 0.005708% | 0.005708%
300 | 28 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
300 | 29 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
300 | 30 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
300 | 31 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
300 | 32 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
300 | 33 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
300 | 34 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
300 | 35 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
300 | 36 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
300 | 37 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
300 | 38 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
300 | 39 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
300 | 40 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
330 | 0 | 0.01142% | 2 | 0.005708% | 1 | 0.005708% | 0.005708% | 0.005708% | 0.005708% | 0.01142% | 0.01142% | 0.01142% | 0.01142% | 0.005708% | 0.005708%
330 | 1 | 0.05709% | 10 | 0.1027% | 18 | 0.1027% | 0.1027% | 0.1027% | 0.1027% | 0.05709% | 0.05709% | 0.05709% | 0.05709% | 0.1027% | 0.1027%
330 | 2 | 0.2227% | 39 | 0.2911% | 51 | 0.2511% | 0.2911% | 0.2911% | 0.2911% | 0.2227% | 0.2227% | 0.2227% | 0.2227% | 0.2511% | 0.2911%
330 | 3 | 0.5709% | 100 | 0.5594% | 98 | 0.5993% | 0.5594% | 0.5594% | 0.5594% | 0.5709% | 0.5309% | 0.5709% | 0.5709% | 0.5993% | 0.5594%
330 | 4 | 0.5937% | 104 | 0.9817% | 172 | 0.9817% | 0.9817% | 0.9817% | 0.9817% | 0.588% | 0.628% | 0.5937% | 0.5937% | 0.9817% | 0.9817%
330 | 5 | 0.7308% | 128 | 0.8333% | 146 | 0.8333% | 0.8333% | 0.8333% | 0.8333% | 0.7308% | 0.7308% | 0.7308% | 0.7308% | 0.8333% | 0.8333%
330 | 6 | 0.7707% | 135 | 1.199% | 210 | 1.187% | 1.193% | 1.193% | 1.193% | 0.7764% | 0.7764% | 0.7707% | 0.7707% | 1.187% | 1.193%
330 | 7 | 0.8849% | 155 | 1.09% | 191 | 1.09% | 1.084% | 1.09% | 1.084% | 0.8849% | 0.8849% | 0.8849% | 0.8849% | 1.09% | 1.09%
330 | 8 | 0.9591% | 168 | 1.147% | 201 | 1.107% | 1.107% | 1.153% | 1.107% | 0.9534% | 0.9534% | 0.9591% | 0.9591% | 1.107% | 1.153%
330 | 9 | 1.045% | 183 | 0.8505% | 149 | 0.8904% | 0.9018% | 0.8505% | 0.9018% | 1.05% | 1.05% | 1.045% | 1.045% | 0.8904% | 0.8505%
330 | 10 | 0.9648% | 169 | 0.7135% | 125 | 0.7192% | 0.7078% | 0.7135% | 0.7078% | 0.9648% | 0.8792% | 0.9648% | 0.9648% | 0.7192% | 0.7135%
330 | 11 | 0.7821% | 137 | 0.5251% | 92 | 0.5194% | 0.5251% | 0.5194% | 0.5251% | 0.7821% | 0.8678% | 0.7821% | 0.7821% | 0.5194% | 0.5194%
330 | 12 | 0.6166% | 108 | 0.371% | 65 | 0.371% | 0.371% | 0.371% | 0.371% | 0.6166% | 0.6109% | 0.6166% | 0.6166% | 0.371% | 0.371%
330 | 13 | 0.2569% | 45 | 0.3025% | 53 | 0.3025% | 0.3082% | 0.3082% | 0.3082% | 0.2569% | 0.2626% | 0.2569% | 0.2569% | 0.3025% | 0.3082%
330 | 14 | 0.3882% | 68 | 0.1826% | 32 | 0.1826% | 0.1712% | 0.1826% | 0.1712% | 0.3882% | 0.3882% | 0.3882% | 0.3882% | 0.1826% | 0.1826%
330 | 15 | 0.1713% | 30 | 0.07991% | 14 | 0.07991% | 0.08562% | 0.0742% | 0.08562% | 0.1313% | 0.1313% | 0.1713% | 0.1713% | 0.07991% | 0.0742%
330 | 16 | 0.1028% | 18 | 0.1084% | 19 | 0.1199% | 0.1142% | 0.1142% | 0.1142% | 0.1427% | 0.1427% | 0.1028% | 0.1028% | 0.1199% | 0.1142%
330 | 17 | 0.1028% | 18 | 0.05708% | 10 | 0.05708% | 0.05708% | 0.05708% | 0.05708% | 0.1028% | 0.09135% | 0.1028% | 0.1028% | 0.05708% | 0.05708%
330 | 18 | 0.01713% | 3 | 0.06279% | 11 | 0.05708% | 0.06279% | 0.06279% | 0.06279% | 0.01713% | 0.02855% | 0.01713% | 0.01713% | 0.05708% | 0.06279%
330 | 19 | 0.03425% | 6 | 0.04566% | 8 | 0.04566% | 0.03995% | 0.04566% | 0.03995% | 0.03425% | 0.03425% | 0.03425% | 0.03425% | 0.04566% | 0.04566%
330 | 20 | 0.04567% | 8 | 0.03995% | 7 | 0.04566% | 0.04566% | 0.03995% | 0.04566% | 0.04567% | 0.04567% | 0.04567% | 0.04567% | 0.04566% | 0.03995%
330 | 21 | 0.04567% | 8 | 0.05708% | 10 | 0.05708% | 0.05708% | 0.05708% | 0.05708% | 0.04567% | 0.04567% | 0.04567% | 0.04567% | 0.05708% | 0.05708%
330 | 22 | 0.02284% | 4 | 0.01712% | 3 | 0.01712% | 0.01712% | 0.01712% | 0.01712% | 0.01142% | 0.01142% | 0.02284% | 0.02284% | 0.01712% | 0.01712%
330 | 23 | 0.01713% | 3 | 0.005708% | 1 | 0.005708% | 0.005708% | 0.005708% | 0.005708% | 0.01142% | 0.01142% | 0% | 0% | 0.005708% | 0.005708%
330 | 24 | 0.005709% | 1 | 0.005708% | 1 | 0.005708% | 0.005708% | 0.005708% | 0.005708% | 0.01713% | 0.01142% | 0.01713% | 0.01713% | 0.005708% | 0.005708%
330 | 25 | 0% | 0 | 0% | 0 | 0% | 0% | 0% | 0% | 0.005709% | 0.01142% | 0.005709% | 0.005709% | 0% | 0%
330 | 26 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
330 | 27 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
330 | 28 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
330 | 29 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
330 | 30 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
330 | 31 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
330 | 32 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
330 | 33 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
330 | 34 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
330 | 35 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
330 | 36 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
330 | 37 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
330 | 38 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
330 | 39 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108
330 | 40 | 0% | 0 | 0% | 0 | bar: Wind Turbine 97 to Wind Turbine 108

## WS Weibull
Annual Wind Speed Weibull Distribution
|  | Measurement Device |  | Wind Turbine
Wind Direction (Midpoint) (°) | Weibull parameter | Gobblers Knob West | Gobblers Knob East | 97 | 98 | 100 | 102 | 103 | 104 | 105 | 106 | 107 | 108
All | Scale Parameter (m/s) [C] | 9.4992 | 9.5613 | 9.6065 | 9.5839 | 9.5726 | 9.5839 | 9.5669 | 9.5782 | 9.5556 | 9.5556 | 9.6065 | 9.5726
0 | Scale Parameter (m/s) [C] | 8.8717 | 8.837 | 8.8788 | 8.8579 | 8.8475 | 8.8579 | 8.935 | 8.9455 | 8.9244 | 8.9244 | 8.8788 | 8.8475
30 | Scale Parameter (m/s) [C] | 7.3762 | 8.5997 | 8.6403 | 8.62 | 8.6098 | 8.62 | 7.4288 | 7.4376 | 7.42 | 7.42 | 8.6403 | 8.6098
60 | Scale Parameter (m/s) [C] | 7.1908 | 7.8301 | 7.8671 | 7.8486 | 7.8393 | 7.8486 | 7.242 | 7.2506 | 7.2335 | 7.2335 | 7.8671 | 7.8393
90 | Scale Parameter (m/s) [C] | 7.6734 | 7.8929 | 7.9302 | 7.9116 | 7.9023 | 7.9116 | 7.7281 | 7.7372 | 7.719 | 7.719 | 7.9302 | 7.9023
120 | Scale Parameter (m/s) [C] | 8.9977 | 9.1118 | 9.1548 | 9.1333 | 9.1226 | 9.1333 | 9.0618 | 9.0725 | 9.0511 | 9.0511 | 9.1548 | 9.1226
150 | Scale Parameter (m/s) [C] | 10.4573 | 10.3311 | 10.3799 | 10.3555 | 10.3433 | 10.3555 | 10.5318 | 10.5442 | 10.5194 | 10.5194 | 10.3799 | 10.3433
180 | Scale Parameter (m/s) [C] | 10.9493 | 11.267 | 11.3202 | 11.2936 | 11.2803 | 11.2936 | 11.0274 | 11.0404 | 11.0143 | 11.0143 | 11.3202 | 11.2803
210 | Scale Parameter (m/s) [C] | 9.3572 | 10.7275 | 10.7781 | 10.7528 | 10.7401 | 10.7528 | 9.4239 | 9.435 | 9.4128 | 9.4128 | 10.7781 | 10.7401
240 | Scale Parameter (m/s) [C] | 9.2094 | 9.6427 | 9.6883 | 9.6655 | 9.6541 | 9.6655 | 9.275 | 9.286 | 9.2641 | 9.2641 | 9.6883 | 9.6541
270 | Scale Parameter (m/s) [C] | 9.9616 | 9.4361 | 9.4807 | 9.4584 | 9.4473 | 9.4584 | 10.0326 | 10.0444 | 10.0208 | 10.0208 | 9.4807 | 9.4473
300 | Scale Parameter (m/s) [C] | 9.5122 | 8.8226 | 8.8642 | 8.8434 | 8.833 | 8.8434 | 9.58 | 9.5913 | 9.5687 | 9.5687 | 8.8642 | 8.833
330 | Scale Parameter (m/s) [C] | 9.6234 | 8.7299 | 8.7711 | 8.7505 | 8.7402 | 8.7505 | 9.692 | 9.7034 | 9.6806 | 9.6806 | 8.7711 | 8.7402
All | Shape Parameter (-) [k] | 2.4084 | 2.3446 | 2.3446 | 2.3446 | 2.3446 | 2.3446 | 2.4084 | 2.4084 | 2.4084 | 2.4084 | 2.3446 | 2.3446
0 | Shape Parameter (-) [k] | 2.0041 | 2.149 | 2.149 | 2.149 | 2.149 | 2.149 | 2.0041 | 2.0041 | 2.0041 | 2.0041 | 2.149 | 2.149
30 | Shape Parameter (-) [k] | 2.0103 | 2.1697 | 2.1697 | 2.1697 | 2.1697 | 2.1697 | 2.0103 | 2.0103 | 2.0103 | 2.0103 | 2.1697 | 2.1697
60 | Shape Parameter (-) [k] | 2.1767 | 2.1455 | 2.1455 | 2.1455 | 2.1455 | 2.1455 | 2.1767 | 2.1767 | 2.1767 | 2.1767 | 2.1455 | 2.1455
90 | Shape Parameter (-) [k] | 2.5372 | 2.3589 | 2.3589 | 2.3589 | 2.3589 | 2.3589 | 2.5372 | 2.5372 | 2.5372 | 2.5372 | 2.3589 | 2.3589
120 | Shape Parameter (-) [k] | 2.6122 | 2.571 | 2.571 | 2.571 | 2.571 | 2.571 | 2.6122 | 2.6122 | 2.6122 | 2.6122 | 2.571 | 2.571
150 | Shape Parameter (-) [k] | 2.7865 | 2.5832 | 2.5832 | 2.5832 | 2.5832 | 2.5832 | 2.7865 | 2.7865 | 2.7865 | 2.7865 | 2.5832 | 2.5832
180 | Shape Parameter (-) [k] | 2.6116 | 2.6117 | 2.6117 | 2.6117 | 2.6117 | 2.6117 | 2.6116 | 2.6116 | 2.6116 | 2.6116 | 2.6117 | 2.6117
210 | Shape Parameter (-) [k] | 2.8085 | 2.5932 | 2.5932 | 2.5932 | 2.5932 | 2.5932 | 2.8085 | 2.8085 | 2.8085 | 2.8085 | 2.5932 | 2.5932
240 | Shape Parameter (-) [k] | 2.5386 | 2.2628 | 2.2628 | 2.2628 | 2.2628 | 2.2628 | 2.5386 | 2.5386 | 2.5386 | 2.5386 | 2.2628 | 2.2628
270 | Shape Parameter (-) [k] | 2.5237 | 2.5745 | 2.5745 | 2.5745 | 2.5745 | 2.5745 | 2.5237 | 2.5237 | 2.5237 | 2.5237 | 2.5745 | 2.5745
300 | Shape Parameter (-) [k] | 2.5066 | 2.3691 | 2.3691 | 2.3691 | 2.3691 | 2.3691 | 2.5066 | 2.5066 | 2.5066 | 2.5066 | 2.3691 | 2.3691
330 | Shape Parameter (-) [k] | 2.3528 | 2.1685 | 2.1685 | 2.1685 | 2.1685 | 2.1685 | 2.3528 | 2.3528 | 2.3528 | 2.3528 | 2.1685 | 2.1685
0 | Frequency (%) | 7.33% | 5.394% | 5.394% | 5.394% | 5.394% | 5.394% | 7.33% | 7.33% | 7.33% | 7.33% | 5.394% | 5.394%
30 | Frequency (%) | 4.727% | 4.994% | 4.994% | 4.994% | 4.994% | 4.994% | 4.727% | 4.727% | 4.727% | 4.727% | 4.994% | 4.994%
60 | Frequency (%) | 3.911% | 4.241% | 4.241% | 4.241% | 4.241% | 4.241% | 3.911% | 3.911% | 3.911% | 3.911% | 4.241% | 4.241%
90 | Frequency (%) | 4.013% | 3.699% | 3.699% | 3.699% | 3.699% | 3.699% | 4.013% | 4.013% | 4.013% | 4.013% | 3.699% | 3.699%
120 | Frequency (%) | 8.215% | 6.969% | 6.969% | 6.969% | 6.969% | 6.969% | 8.215% | 8.215% | 8.215% | 8.215% | 6.969% | 6.969%
150 | Frequency (%) | 12.74% | 11.62% | 11.62% | 11.62% | 11.62% | 11.62% | 12.74% | 12.74% | 12.74% | 12.74% | 11.62% | 11.62%
180 | Frequency (%) | 13.52% | 14.18% | 14.18% | 14.18% | 14.18% | 14.18% | 13.52% | 13.52% | 13.52% | 13.52% | 14.18% | 14.18%
210 | Frequency (%) | 8.963% | 7.803% | 7.803% | 7.803% | 7.803% | 7.803% | 8.963% | 8.963% | 8.963% | 8.963% | 7.803% | 7.803%
240 | Frequency (%) | 7.747% | 7.089% | 7.089% | 7.089% | 7.089% | 7.089% | 7.747% | 7.747% | 7.747% | 7.747% | 7.089% | 7.089%
270 | Frequency (%) | 8.455% | 12.21% | 12.21% | 12.21% | 12.21% | 12.21% | 8.455% | 8.455% | 8.455% | 8.455% | 12.21% | 12.21%
300 | Frequency (%) | 10.96% | 12.16% | 12.16% | 12.16% | 12.16% | 12.16% | 10.96% | 10.96% | 10.96% | 10.96% | 12.16% | 12.16%
330 | Frequency (%) | 9.42% | 9.635% | 9.635% | 9.635% | 9.635% | 9.635% | 9.42% | 9.42% | 9.42% | 9.42% | 9.635% | 9.635%

## Ambient Mean TI
Mean Turbulence Intensity (10-minute WS SD/10-minute mean WS) [%] {I(wind speed, direction)}
|  | Measurement Device |  | Wind Turbine
Wind Direction (Midpoint) (°) | Wind Speed (Midpoint) (m/s) | Gobblers Knob West | Gobblers Knob East | 97 | 98 | 100 | 102 | 103 | 104 | 105 | 106 | 107 | 108
ALL | 0 | 73.07% | 114.7% | 114.7% | 114.7% | 114.7% | 114.7% | 73.07% | 73.07% | 73.07% | 73.07% | 114.7% | 114.7%
ALL | 1 | 70.36% | 75.24% | 75.35% | 75.24% | 75.24% | 75.24% | 70.42% | 70.42% | 70.42% | 70.42% | 75.35% | 75.24%
ALL | 2 | 51.7% | 49.74% | 50.72% | 49.74% | 49.74% | 49.74% | 51.76% | 51.74% | 51.76% | 51.76% | 50.72% | 49.74%
ALL | 3 | 36.23% | 35.23% | 35.62% | 35.27% | 35.25% | 35.27% | 36.41% | 36.49% | 36.41% | 36.41% | 35.62% | 35.25%
ALL | 4 | 27.9% | 26.72% | 26.72% | 26.72% | 26.72% | 26.72% | 28.25% | 28.25% | 28.25% | 28.25% | 26.72% | 26.72%
ALL | 5 | 22.53% | 21.69% | 21.68% | 21.69% | 21.69% | 21.69% | 22.81% | 22.81% | 22.81% | 22.81% | 21.68% | 21.69%
ALL | 6 | 18.63% | 18.04% | 18.07% | 18.05% | 18.05% | 18.05% | 18.73% | 18.73% | 18.73% | 18.73% | 18.07% | 18.05%
ALL | 7 | 15.97% | 15.44% | 15.47% | 15.47% | 15.46% | 15.47% | 16.01% | 16.01% | 16.01% | 16.01% | 15.47% | 15.46%
ALL | 8 | 14.11% | 13.58% | 13.74% | 13.73% | 13.58% | 13.73% | 14.23% | 14.23% | 14.23% | 14.23% | 13.74% | 13.58%
ALL | 9 | 13.03% | 12.57% | 12.51% | 12.5% | 12.58% | 12.5% | 13.08% | 13.08% | 13.03% | 13.03% | 12.51% | 12.58%
ALL | 10 | 12.11% | 11.36% | 11.34% | 11.35% | 11.36% | 11.35% | 12.15% | 12.15% | 12.14% | 12.14% | 11.34% | 11.36%
ALL | 11 | 11.31% | 10.67% | 10.71% | 10.69% | 10.68% | 10.69% | 11.39% | 11.39% | 11.38% | 11.38% | 10.71% | 10.68%
ALL | 12 | 11.29% | 10.21% | 10.2% | 10.2% | 10.2% | 10.2% | 11.22% | 11.24% | 11.23% | 11.23% | 10.2% | 10.2%
ALL | 13 | 11.42% | 9.681% | 9.737% | 9.693% | 9.685% | 9.693% | 11.5% | 11.54% | 11.49% | 11.49% | 9.737% | 9.685%
ALL | 14 | 11.6% | 9.763% | 9.646% | 9.676% | 9.763% | 9.676% | 11.62% | 11.56% | 11.64% | 11.64% | 9.646% | 9.763%
ALL | 15 | 11.32% | 9.754% | 9.726% | 9.774% | 9.628% | 9.774% | 11.27% | 11.21% | 11.27% | 11.27% | 9.726% | 9.628%
ALL | 16 | 11.36% | 10.2% | 10.29% | 10.3% | 10.32% | 10.3% | 11.34% | 11.44% | 11.32% | 11.32% | 10.29% | 10.32%
ALL | 17 | 12.19% | 10.93% | 10.84% | 10.91% | 10.87% | 10.91% | 12.41% | 12.33% | 12.44% | 12.44% | 10.84% | 10.87%
ALL | 18 | 10.7% | 10.03% | 9.9% | 10.01% | 10.03% | 10.01% | 10.76% | 11.1% | 10.74% | 10.74% | 9.9% | 10.03%
ALL | 19 | 11.35% | 10.42% | 10.83% | 10.33% | 10.42% | 10.33% | 11.21% | 11.25% | 11.21% | 11.21% | 10.83% | 10.42%
ALL | 20 | 11.42% | 9.728% | 9.843% | 9.843% | 9.728% | 9.843% | 11.54% | 11.44% | 11.54% | 11.54% | 9.843% | 9.728%
ALL | 21 | 11.23% | 10.03% | 9.881% | 9.881% | 9.936% | 9.881% | 11.18% | 11.05% | 11.18% | 11.18% | 9.881% | 9.936%
ALL | 22 | 10.37% | 11.4% | 11.33% | 11.33% | 11.33% | 11.33% | 10.41% | 10.74% | 10.41% | 10.41% | 11.33% | 11.33%
ALL | 23 | 10.74% | 9.155% | 9.334% | 9.155% | 9.155% | 9.155% | 10.9% | 10.9% | 10.9% | 10.9% | 9.334% | 9.155%
ALL | 24 | 10.47% | 6.417% | 6.743% | 6.417% | 6.417% | 6.417% | 11.57% | 11.57% | 11.57% | 11.57% | 6.743% | 6.417%
ALL | 25 | 8.123% | 8.395% | 8.395% | 8.395% | 8.395% | 8.395% | 8.07% | 8.07% | 8.07% | 8.07% | 8.395% | 8.395%
ALL | 26 | 22.36% | 9.739% | 9.739% | 9.739% | 9.739% | 9.739% | 22.36% | 22.36% | 22.36% | 22.36% | 9.739% | 9.739%
ALL | 27 | 9.924% | 9.743% | 9.743% | 9.743% | 9.743% | 9.743% | 9.924% | 9.924% | 9.924% | 9.924% | 9.743% | 9.743%
ALL | 28 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
ALL | 29 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
ALL | 30 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
ALL | 31 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
ALL | 32 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
ALL | 33 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
ALL | 34 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
ALL | 35 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
ALL | 36 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
ALL | 37 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
ALL | 38 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
ALL | 39 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
ALL | 40 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
0 | 0 | 67.47% | 149.1% | 149.1% | 149.1% | 149.1% | 149.1% | 67.47% | 67.47% | 67.47% | 67.47% | 149.1% | 149.1%
0 | 1 | 68.5% | 76.43% | 76.43% | 76.43% | 76.43% | 76.43% | 68.5% | 68.5% | 68.5% | 68.5% | 76.43% | 76.43%
0 | 2 | 53.79% | 59.28% | 59.79% | 59.28% | 59.28% | 59.28% | 53.79% | 53.79% | 53.79% | 53.79% | 59.79% | 59.28%
0 | 3 | 37.22% | 35.15% | 35.97% | 35.15% | 35.15% | 35.15% | 37.22% | 37.3% | 37.22% | 37.22% | 35.97% | 35.15%
0 | 4 | 28.93% | 29.2% | 29.2% | 29.2% | 29.2% | 29.2% | 28.93% | 29.29% | 28.93% | 28.93% | 29.2% | 29.2%
0 | 5 | 23.29% | 21.1% | 21.1% | 21.1% | 21.1% | 21.1% | 23.29% | 23.29% | 23.29% | 23.29% | 21.1% | 21.1%
0 | 6 | 19.65% | 19.69% | 19.69% | 19.69% | 19.69% | 19.69% | 19.65% | 19.69% | 19.65% | 19.65% | 19.69% | 19.69%
0 | 7 | 18.42% | 18.75% | 18.85% | 18.85% | 18.85% | 18.85% | 18.42% | 18.4% | 18.42% | 18.42% | 18.85% | 18.85%
0 | 8 | 16.89% | 15.94% | 16% | 16% | 15.85% | 16% | 16.89% | 16.89% | 16.89% | 16.89% | 16% | 15.85%
0 | 9 | 15.15% | 16.02% | 15.9% | 15.9% | 16.02% | 15.9% | 15.15% | 15.15% | 15.15% | 15.15% | 15.9% | 16.02%
0 | 10 | 15.71% | 14.62% | 14.62% | 14.62% | 14.62% | 14.62% | 15.71% | 15.71% | 15.71% | 15.71% | 14.62% | 14.62%
0 | 11 | 13.76% | 13.84% | 13.84% | 13.84% | 13.84% | 13.84% | 13.76% | 14.05% | 13.76% | 13.76% | 13.84% | 13.84%
0 | 12 | 13.65% | 13.3% | 13.34% | 13.3% | 13.3% | 13.3% | 13.65% | 13.65% | 13.65% | 13.65% | 13.34% | 13.3%
0 | 13 | 13.34% | 12.3% | 12.21% | 12.3% | 12.3% | 12.3% | 13.34% | 13.34% | 13.34% | 13.34% | 12.21% | 12.3%
0 | 14 | 12.66% | 12.82% | 12.94% | 12.91% | 12.82% | 12.91% | 12.66% | 12.66% | 12.66% | 12.66% | 12.94% | 12.82%
0 | 15 | 13.06% | 13.23% | 13.29% | 13.29% | 13.55% | 13.29% | 13.23% | 13.23% | 13.06% | 13.06% | 13.29% | 13.55%
0 | 16 | 13.36% | 14.54% | 13.98% | 13.98% | 13.98% | 13.98% | 13.02% | 13.02% | 13.36% | 13.36% | 13.98% | 13.98%
0 | 17 | 15.7% | 12.85% | 12.93% | 12.85% | 12.85% | 12.85% | 15.7% | 15.7% | 15.7% | 15.7% | 12.93% | 12.85%
0 | 18 | 11.53% | 11.08% | 11.29% | 11.08% | 11.08% | 11.08% | 11.53% | 11.53% | 11.53% | 11.53% | 11.29% | 11.08%
0 | 19 | 10.77% | 11.1% | 11.1% | 11.1% | 11.1% | 11.1% | 10.82% | 10.82% | 10.77% | 10.77% | 11.1% | 11.1%
0 | 20 | 15.24% | 10.12% | 10.12% | 10.12% | 10.12% | 10.12% | 14.27% | 14.27% | 15.24% | 15.24% | 10.12% | 10.12%
0 | 21 | 10.12% | 9.155% | 9.155% | 9.155% | 9.155% | 9.155% | 10.12% | 10.12% | 10.12% | 10.12% | 9.155% | 9.155%
0 | 22 | 10.72% | 31.96% | 31.96% | 31.96% | 31.96% | 31.96% | 10.72% | 10.72% | 10.72% | 10.72% | 31.96% | 31.96%
0 | 23 | 7.08% | 0% | 0% | 0% | 0% | 0% | 7.08% | 7.08% | 7.08% | 7.08% | 0% | 0%
0 | 24 | 8.044% | 0% | 0% | 0% | 0% | 0% | 8.044% | 8.044% | 8.044% | 8.044% | 0% | 0%
0 | 25 | 7.819% | 0% | 0% | 0% | 0% | 0% | 7.819% | 7.819% | 7.819% | 7.819% | 0% | 0%
0 | 26 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
0 | 27 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
0 | 28 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
0 | 29 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
0 | 30 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
0 | 31 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
0 | 32 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
0 | 33 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
0 | 34 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
0 | 35 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
0 | 36 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
0 | 37 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
0 | 38 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
0 | 39 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
0 | 40 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
30 | 0 | 154.4% | 163.5% | 163.5% | 163.5% | 163.5% | 163.5% | 154.4% | 154.4% | 154.4% | 154.4% | 163.5% | 163.5%
30 | 1 | 72.19% | 92.2% | 92.2% | 92.2% | 92.2% | 92.2% | 72.19% | 72.19% | 72.19% | 72.19% | 92.2% | 92.2%
30 | 2 | 54.15% | 49.16% | 49.46% | 49.16% | 49.16% | 49.16% | 54.15% | 54.15% | 54.15% | 54.15% | 49.46% | 49.16%
30 | 3 | 35.53% | 36.49% | 37.16% | 36.49% | 36.49% | 36.49% | 35.53% | 35.17% | 35.53% | 35.53% | 37.16% | 36.49%
30 | 4 | 28.41% | 28.52% | 28.52% | 28.52% | 28.52% | 28.52% | 28.41% | 29.25% | 28.41% | 28.41% | 28.52% | 28.52%
30 | 5 | 23.72% | 21.93% | 21.93% | 21.93% | 21.93% | 21.93% | 23.72% | 23.72% | 23.72% | 23.72% | 21.93% | 21.93%
30 | 6 | 19.8% | 20.77% | 20.88% | 20.83% | 20.83% | 20.83% | 19.8% | 19.8% | 19.8% | 19.8% | 20.88% | 20.83%
30 | 7 | 17.19% | 16.91% | 16.99% | 17% | 16.89% | 17% | 17.19% | 17.19% | 17.19% | 17.19% | 16.99% | 16.89%
30 | 8 | 16.23% | 16.75% | 16.44% | 16.44% | 16.75% | 16.44% | 16.3% | 16.3% | 16.23% | 16.23% | 16.44% | 16.75%
30 | 9 | 16.78% | 15.26% | 15.48% | 15.48% | 15.26% | 15.48% | 16.69% | 16.69% | 16.78% | 16.78% | 15.48% | 15.26%
30 | 10 | 16.18% | 15.93% | 16.21% | 16.07% | 15.93% | 16.07% | 16.18% | 16.43% | 16.18% | 16.18% | 16.21% | 15.93%
30 | 11 | 16.57% | 13.56% | 13.48% | 13.51% | 13.56% | 13.51% | 16.57% | 16.17% | 16.57% | 16.57% | 13.48% | 13.56%
30 | 12 | 13.11% | 14.77% | 14.76% | 14.85% | 14.85% | 14.85% | 13.11% | 13.11% | 13.11% | 13.11% | 14.76% | 14.85%
30 | 13 | 17.85% | 12.33% | 12.41% | 12.29% | 12.29% | 12.29% | 17.85% | 17.85% | 17.85% | 17.85% | 12.41% | 12.29%
30 | 14 | 16.07% | 11.64% | 11.67% | 11.45% | 11.64% | 11.45% | 16.07% | 16.07% | 16.07% | 16.07% | 11.67% | 11.64%
30 | 15 | 22.62% | 14.88% | 12.72% | 13.52% | 13.33% | 13.52% | 22.62% | 22.62% | 22.62% | 22.62% | 12.72% | 13.33%
30 | 16 | 16.61% | 10.96% | 14.09% | 14.16% | 14.16% | 14.16% | 16.61% | 16.61% | 16.61% | 16.61% | 14.09% | 14.16%
30 | 17 | 13.24% | 12.28% | 13.1% | 13.1% | 11.51% | 13.1% | 13.24% | 13.24% | 13.24% | 13.24% | 13.1% | 11.51%
30 | 18 | 0% | 12.67% | 11.17% | 11.17% | 12.67% | 11.17% | 0% | 0% | 0% | 0% | 11.17% | 12.67%
30 | 19 | 0% | 11.12% | 11.12% | 11.12% | 11.12% | 11.12% | 0% | 0% | 0% | 0% | 11.12% | 11.12%
30 | 20 | 0% | 7.508% | 7.508% | 7.508% | 7.508% | 7.508% | 0% | 0% | 0% | 0% | 7.508% | 7.508%
30 | 21 | 8.166% | 7.287% | 7.287% | 7.287% | 7.287% | 7.287% | 8.166% | 8.166% | 8.166% | 8.166% | 7.287% | 7.287%
30 | 22 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
30 | 23 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
30 | 24 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
30 | 25 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
30 | 26 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
30 | 27 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
30 | 28 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
30 | 29 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
30 | 30 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
30 | 31 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
30 | 32 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
30 | 33 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
30 | 34 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
30 | 35 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
30 | 36 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
30 | 37 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
30 | 38 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
30 | 39 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
30 | 40 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
60 | 0 | 193.3% | 0% | 0% | 0% | 0% | 0% | 193.3% | 193.3% | 193.3% | 193.3% | 0% | 0%
60 | 1 | 68.23% | 80.08% | 80.08% | 80.08% | 80.08% | 80.08% | 68.23% | 68.23% | 68.23% | 68.23% | 80.08% | 80.08%
60 | 2 | 52.3% | 54.08% | 56.77% | 54.08% | 54.08% | 54.08% | 52.3% | 52.3% | 52.3% | 52.3% | 56.77% | 54.08%
60 | 3 | 36.45% | 36.06% | 35.45% | 36.06% | 36.06% | 36.06% | 36.45% | 37.1% | 36.45% | 36.45% | 35.45% | 36.06%
60 | 4 | 28.13% | 26.68% | 26.68% | 26.68% | 26.68% | 26.68% | 28.13% | 27.94% | 28.13% | 28.13% | 26.68% | 26.68%
60 | 5 | 23.94% | 24.09% | 24.09% | 24.09% | 24.09% | 24.09% | 24.05% | 23.74% | 23.94% | 23.94% | 24.09% | 24.09%
60 | 6 | 18.74% | 18.98% | 18.98% | 18.98% | 18.98% | 18.98% | 18.69% | 19.08% | 18.74% | 18.74% | 18.98% | 18.98%
60 | 7 | 15.86% | 16.76% | 16.76% | 16.76% | 16.76% | 16.76% | 15.86% | 15.86% | 15.86% | 15.86% | 16.76% | 16.76%
60 | 8 | 14.27% | 12.68% | 12.96% | 12.96% | 12.72% | 12.96% | 14.27% | 14.27% | 14.27% | 14.27% | 12.96% | 12.72%
60 | 9 | 14.9% | 13.58% | 13.13% | 13.13% | 13.5% | 13.13% | 14.9% | 14.9% | 14.9% | 14.9% | 13.13% | 13.5%
60 | 10 | 12.24% | 13.02% | 13.02% | 13.02% | 13.02% | 13.02% | 12.24% | 12.39% | 12.24% | 12.24% | 13.02% | 13.02%
60 | 11 | 12.79% | 11.98% | 11.98% | 11.98% | 11.98% | 11.98% | 12.79% | 12.55% | 12.79% | 12.79% | 11.98% | 11.98%
60 | 12 | 12.18% | 10.81% | 10.72% | 10.81% | 10.81% | 10.81% | 12.18% | 12.18% | 12.18% | 12.18% | 10.72% | 10.81%
60 | 13 | 11.51% | 11.23% | 11.56% | 11.23% | 11.23% | 11.23% | 11.51% | 11.51% | 11.51% | 11.51% | 11.56% | 11.23%
60 | 14 | 14.51% | 11.98% | 11.87% | 12.12% | 11.98% | 12.12% | 14.51% | 14.51% | 14.51% | 14.51% | 11.87% | 11.98%
60 | 15 | 12.76% | 10.34% | 10.32% | 10.32% | 10.34% | 10.32% | 12.76% | 12.76% | 12.76% | 12.76% | 10.32% | 10.34%
60 | 16 | 11.03% | 9.016% | 9.016% | 9.016% | 9.016% | 9.016% | 11.03% | 11.03% | 11.03% | 11.03% | 9.016% | 9.016%
60 | 17 | 0% | 19.46% | 19.46% | 19.46% | 19.46% | 19.46% | 0% | 0% | 0% | 0% | 19.46% | 19.46%
60 | 18 | 0% | 8.448% | 8.448% | 8.448% | 8.448% | 8.448% | 0% | 0% | 0% | 0% | 8.448% | 8.448%
60 | 19 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
60 | 20 | 0% | 8.671% | 8.671% | 8.671% | 8.671% | 8.671% | 0% | 0% | 0% | 0% | 8.671% | 8.671%
60 | 21 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
60 | 22 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
60 | 23 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
60 | 24 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
60 | 25 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
60 | 26 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
60 | 27 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
60 | 28 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
60 | 29 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
60 | 30 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
60 | 31 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
60 | 32 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
60 | 33 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
60 | 34 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
60 | 35 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
60 | 36 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
60 | 37 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
60 | 38 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
60 | 39 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
60 | 40 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
90 | 0 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
90 | 1 | 57.78% | 85.24% | 85.24% | 85.24% | 85.24% | 85.24% | 57.78% | 57.78% | 57.78% | 57.78% | 85.24% | 85.24%
90 | 2 | 50.26% | 39.28% | 39.2% | 39.28% | 39.28% | 39.28% | 50.26% | 50.26% | 50.26% | 50.26% | 39.2% | 39.28%
90 | 3 | 34.91% | 31.93% | 32.38% | 31.93% | 31.93% | 31.93% | 34.91% | 34.24% | 34.91% | 34.91% | 32.38% | 31.93%
90 | 4 | 29.75% | 25.7% | 25.58% | 25.7% | 25.7% | 25.7% | 29.75% | 30.51% | 29.75% | 29.75% | 25.58% | 25.7%
90 | 5 | 22.71% | 21.44% | 21.59% | 21.44% | 21.44% | 21.44% | 22.71% | 22.71% | 22.71% | 22.71% | 21.59% | 21.44%
90 | 6 | 18.22% | 18.42% | 18.34% | 18.42% | 18.42% | 18.42% | 18.22% | 18.22% | 18.22% | 18.22% | 18.34% | 18.42%
90 | 7 | 16.54% | 14.78% | 14.78% | 14.78% | 14.78% | 14.78% | 16.54% | 16.54% | 16.54% | 16.54% | 14.78% | 14.78%
90 | 8 | 13.16% | 15.57% | 15.84% | 15.84% | 15.71% | 15.84% | 13.16% | 13.16% | 13.16% | 13.16% | 15.84% | 15.71%
90 | 9 | 12.59% | 12.4% | 12.24% | 12.24% | 12.27% | 12.24% | 12.59% | 12.59% | 12.59% | 12.59% | 12.24% | 12.27%
90 | 10 | 10.97% | 10.22% | 10.22% | 10.22% | 10.22% | 10.22% | 10.97% | 11.21% | 10.97% | 10.97% | 10.22% | 10.22%
90 | 11 | 10.84% | 11.56% | 11.56% | 11.56% | 11.56% | 11.56% | 10.84% | 10.52% | 10.84% | 10.84% | 11.56% | 11.56%
90 | 12 | 12.11% | 12.09% | 12.09% | 12.09% | 12.09% | 12.09% | 12.11% | 12.11% | 12.11% | 12.11% | 12.09% | 12.09%
90 | 13 | 14.19% | 11.4% | 11.6% | 11.4% | 11.4% | 11.4% | 14.19% | 14.19% | 14.19% | 14.19% | 11.6% | 11.4%
90 | 14 | 12.61% | 12.87% | 12.51% | 12.87% | 12.87% | 12.87% | 12.61% | 12.61% | 12.61% | 12.61% | 12.51% | 12.87%
90 | 15 | 0% | 9.918% | 9.918% | 9.918% | 9.918% | 9.918% | 0% | 0% | 0% | 0% | 9.918% | 9.918%
90 | 16 | 9.482% | 0% | 0% | 0% | 0% | 0% | 9.482% | 9.482% | 9.482% | 9.482% | 0% | 0%
90 | 17 | 0% | 8.071% | 8.071% | 8.071% | 8.071% | 8.071% | 0% | 0% | 0% | 0% | 8.071% | 8.071%
90 | 18 | 0% | 6.189% | 6.189% | 6.189% | 6.189% | 6.189% | 0% | 0% | 0% | 0% | 6.189% | 6.189%
90 | 19 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
90 | 20 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
90 | 21 | 0% | 9.558% | 9.558% | 9.558% | 9.558% | 9.558% | 0% | 0% | 0% | 0% | 9.558% | 9.558%
90 | 22 | 0% | 8.368% | 8.368% | 8.368% | 8.368% | 8.368% | 0% | 0% | 0% | 0% | 8.368% | 8.368%
90 | 23 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
90 | 24 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
90 | 25 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
90 | 26 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
90 | 27 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
90 | 28 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
90 | 29 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
90 | 30 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
90 | 31 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
90 | 32 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
90 | 33 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
90 | 34 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
90 | 35 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
90 | 36 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
90 | 37 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
90 | 38 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
90 | 39 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
90 | 40 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
120 | 0 | 0% | 24.44% | 24.44% | 24.44% | 24.44% | 24.44% | 0% | 0% | 0% | 0% | 24.44% | 24.44%
120 | 1 | 68.34% | 86.79% | 90.46% | 86.79% | 86.79% | 86.79% | 68.34% | 68.34% | 68.34% | 68.34% | 90.46% | 86.79%
120 | 2 | 53.53% | 45.5% | 46.01% | 45.5% | 45.5% | 45.5% | 53.53% | 53.53% | 53.53% | 53.53% | 46.01% | 45.5%
120 | 3 | 35.47% | 34.92% | 35.44% | 34.92% | 34.92% | 34.92% | 35.47% | 35.39% | 35.47% | 35.47% | 35.44% | 34.92%
120 | 4 | 27.66% | 28.07% | 28.07% | 28.07% | 28.07% | 28.07% | 27.49% | 28.09% | 27.66% | 27.66% | 28.07% | 28.07%
120 | 5 | 21.32% | 22.27% | 22.27% | 22.27% | 22.27% | 22.27% | 21.46% | 21.46% | 21.32% | 21.32% | 22.27% | 22.27%
120 | 6 | 20.1% | 18.33% | 18.37% | 18.37% | 18.37% | 18.37% | 20.1% | 20.1% | 20.1% | 20.1% | 18.37% | 18.37%
120 | 7 | 16.24% | 14.68% | 14.66% | 14.66% | 14.66% | 14.66% | 16.24% | 16.24% | 16.24% | 16.24% | 14.66% | 14.66%
120 | 8 | 13.86% | 13.38% | 13.44% | 13.44% | 13.42% | 13.44% | 13.86% | 13.86% | 13.86% | 13.86% | 13.44% | 13.42%
120 | 9 | 12.93% | 12.62% | 12.65% | 12.65% | 12.6% | 12.65% | 12.93% | 12.93% | 12.93% | 12.93% | 12.65% | 12.6%
120 | 10 | 11.05% | 10.54% | 10.51% | 10.52% | 10.54% | 10.52% | 11.05% | 11.08% | 11.05% | 11.05% | 10.51% | 10.54%
120 | 11 | 10.02% | 9.874% | 9.89% | 9.874% | 9.874% | 9.874% | 10.02% | 10.14% | 10.02% | 10.02% | 9.89% | 9.874%
120 | 12 | 9.886% | 10.24% | 10.36% | 10.29% | 10.29% | 10.29% | 9.886% | 9.886% | 9.886% | 9.886% | 10.36% | 10.29%
120 | 13 | 10.31% | 10.87% | 10.73% | 10.87% | 10.75% | 10.87% | 10.31% | 10.31% | 10.31% | 10.31% | 10.73% | 10.75%
120 | 14 | 10.45% | 9.217% | 8.598% | 8.598% | 9.217% | 8.598% | 10.45% | 10.45% | 10.45% | 10.45% | 8.598% | 9.217%
120 | 15 | 10.87% | 9.164% | 10.46% | 10.46% | 9.495% | 10.46% | 10.87% | 10.87% | 10.87% | 10.87% | 10.46% | 9.495%
120 | 16 | 10.62% | 9.064% | 8.83% | 8.83% | 8.83% | 8.83% | 10.62% | 10.62% | 10.62% | 10.62% | 8.83% | 8.83%
120 | 17 | 9.915% | 9.906% | 9.812% | 9.906% | 9.906% | 9.906% | 9.915% | 9.915% | 9.915% | 9.915% | 9.812% | 9.906%
120 | 18 | 11.01% | 8.446% | 8.832% | 8.446% | 8.446% | 8.446% | 11.01% | 11.01% | 11.01% | 11.01% | 8.832% | 8.446%
120 | 19 | 9.865% | 0% | 0% | 0% | 0% | 0% | 9.865% | 9.865% | 9.865% | 9.865% | 0% | 0%
120 | 20 | 9.76% | 0% | 0% | 0% | 0% | 0% | 9.76% | 9.76% | 9.76% | 9.76% | 0% | 0%
120 | 21 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
120 | 22 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
120 | 23 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
120 | 24 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
120 | 25 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
120 | 26 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
120 | 27 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
120 | 28 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
120 | 29 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
120 | 30 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
120 | 31 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
120 | 32 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
120 | 33 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
120 | 34 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
120 | 35 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
120 | 36 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
120 | 37 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
120 | 38 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
120 | 39 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
120 | 40 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
150 | 0 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
150 | 1 | 82.18% | 68.41% | 68.41% | 68.41% | 68.41% | 68.41% | 82.18% | 82.18% | 82.18% | 82.18% | 68.41% | 68.41%
150 | 2 | 54.67% | 57.41% | 57.62% | 57.41% | 57.41% | 57.41% | 54.67% | 54.67% | 54.67% | 54.67% | 57.62% | 57.41%
150 | 3 | 38.08% | 35.16% | 36.25% | 35.16% | 35.16% | 35.16% | 38.08% | 38.41% | 38.08% | 38.08% | 36.25% | 35.16%
150 | 4 | 25.26% | 27.88% | 27.88% | 27.88% | 27.88% | 27.88% | 25.26% | 25.88% | 25.26% | 25.26% | 27.88% | 27.88%
150 | 5 | 21.79% | 20.76% | 20.7% | 20.7% | 20.7% | 20.7% | 21.79% | 21.79% | 21.79% | 21.79% | 20.7% | 20.7%
150 | 6 | 18.38% | 17.86% | 17.93% | 17.93% | 17.93% | 17.93% | 18.38% | 18.44% | 18.38% | 18.38% | 17.93% | 17.93%
150 | 7 | 16.4% | 15.43% | 15.43% | 15.43% | 15.43% | 15.43% | 16.4% | 16.38% | 16.4% | 16.4% | 15.43% | 15.43%
150 | 8 | 13.45% | 13.33% | 13.56% | 13.56% | 13.33% | 13.56% | 13.45% | 13.45% | 13.45% | 13.45% | 13.56% | 13.33%
150 | 9 | 12.96% | 13.02% | 12.84% | 12.84% | 13.02% | 12.84% | 12.96% | 12.96% | 12.96% | 12.96% | 12.84% | 13.02%
150 | 10 | 11.62% | 10.57% | 10.49% | 10.58% | 10.57% | 10.58% | 11.62% | 11.5% | 11.62% | 11.62% | 10.49% | 10.57%
150 | 11 | 10.95% | 10.26% | 10.35% | 10.25% | 10.26% | 10.25% | 10.95% | 11.22% | 10.95% | 10.95% | 10.35% | 10.26%
150 | 12 | 10.36% | 9.318% | 9.318% | 9.318% | 9.318% | 9.318% | 10.36% | 10.36% | 10.36% | 10.36% | 9.318% | 9.318%
150 | 13 | 11.3% | 9.375% | 9.346% | 9.367% | 9.375% | 9.367% | 11.3% | 11.31% | 11.3% | 11.3% | 9.346% | 9.375%
150 | 14 | 10.98% | 9.06% | 9.146% | 9.072% | 9.06% | 9.072% | 10.98% | 10.97% | 10.98% | 10.98% | 9.146% | 9.06%
150 | 15 | 10.88% | 8.675% | 8.606% | 8.555% | 8.509% | 8.555% | 10.76% | 10.76% | 10.88% | 10.88% | 8.606% | 8.509%
150 | 16 | 10.32% | 9.059% | 9.083% | 9.308% | 9.308% | 9.308% | 10.62% | 10.62% | 10.32% | 10.32% | 9.083% | 9.308%
150 | 17 | 10.6% | 8.612% | 8.555% | 8.618% | 8.618% | 8.618% | 10.63% | 10.65% | 10.6% | 10.6% | 8.555% | 8.618%
150 | 18 | 8.855% | 7.608% | 7.788% | 7.589% | 7.608% | 7.589% | 8.922% | 9.37% | 8.855% | 8.855% | 7.788% | 7.608%
150 | 19 | 10.5% | 8.173% | 8.132% | 8.132% | 8.173% | 8.132% | 10.5% | 10.17% | 10.5% | 10.5% | 8.132% | 8.173%
150 | 20 | 10.51% | 9.128% | 9.128% | 9.128% | 9.128% | 9.128% | 10.51% | 11.16% | 10.51% | 10.51% | 9.128% | 9.128%
150 | 21 | 10.93% | 9.323% | 9.323% | 9.323% | 9.323% | 9.323% | 10.93% | 10.93% | 10.93% | 10.93% | 9.323% | 9.323%
150 | 22 | 10.09% | 12.13% | 12.13% | 12.13% | 12.13% | 12.13% | 9.998% | 9.998% | 10.09% | 10.09% | 12.13% | 12.13%
150 | 23 | 0% | 8.806% | 8.806% | 8.806% | 8.806% | 8.806% | 10.36% | 10.36% | 0% | 0% | 8.806% | 8.806%
150 | 24 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
150 | 25 | 0% | 8.644% | 8.644% | 8.644% | 8.644% | 8.644% | 0% | 0% | 0% | 0% | 8.644% | 8.644%
150 | 26 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
150 | 27 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
150 | 28 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
150 | 29 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
150 | 30 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
150 | 31 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
150 | 32 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
150 | 33 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
150 | 34 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
150 | 35 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
150 | 36 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
150 | 37 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
150 | 38 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
150 | 39 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
150 | 40 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
180 | 0 | 74.44% | 0% | 0% | 0% | 0% | 0% | 74.44% | 74.44% | 74.44% | 74.44% | 0% | 0%
180 | 1 | 64.8% | 81.24% | 81.24% | 81.24% | 81.24% | 81.24% | 64.8% | 64.8% | 64.8% | 64.8% | 81.24% | 81.24%
180 | 2 | 52.58% | 54.18% | 54.9% | 54.18% | 54.18% | 54.18% | 52.58% | 52.58% | 52.58% | 52.58% | 54.9% | 54.18%
180 | 3 | 32.36% | 37.49% | 37.85% | 37.49% | 37.49% | 37.49% | 32.36% | 33.09% | 32.36% | 32.36% | 37.85% | 37.49%
180 | 4 | 28.6% | 26.68% | 26.68% | 26.68% | 26.68% | 26.68% | 28.6% | 28.3% | 28.6% | 28.6% | 26.68% | 26.68%
180 | 5 | 21.24% | 22.88% | 22.77% | 22.88% | 22.88% | 22.88% | 21.24% | 21.24% | 21.24% | 21.24% | 22.77% | 22.88%
180 | 6 | 17.44% | 19.25% | 19.48% | 19.38% | 19.32% | 19.38% | 17.44% | 17.44% | 17.44% | 17.44% | 19.48% | 19.32%
180 | 7 | 14.82% | 15.55% | 15.59% | 15.59% | 15.57% | 15.59% | 14.82% | 14.84% | 14.82% | 14.82% | 15.59% | 15.57%
180 | 8 | 14.44% | 13.49% | 13.4% | 13.41% | 13.41% | 13.41% | 14.46% | 14.46% | 14.44% | 14.44% | 13.4% | 13.41%
180 | 9 | 13.14% | 12.63% | 12.71% | 12.69% | 12.68% | 12.69% | 13.13% | 13.13% | 13.14% | 13.14% | 12.71% | 12.68%
180 | 10 | 12.98% | 11.31% | 11.37% | 11.34% | 11.31% | 11.34% | 12.98% | 13.04% | 12.98% | 12.98% | 11.37% | 11.31%
180 | 11 | 12.64% | 10.14% | 10.12% | 10.12% | 10.14% | 10.12% | 12.64% | 12.61% | 12.64% | 12.64% | 10.12% | 10.14%
180 | 12 | 12.01% | 9.678% | 9.681% | 9.678% | 9.678% | 9.678% | 12.01% | 12.01% | 12.01% | 12.01% | 9.681% | 9.678%
180 | 13 | 11.83% | 9.863% | 9.885% | 9.872% | 9.863% | 9.872% | 11.83% | 11.81% | 11.83% | 11.83% | 9.885% | 9.863%
180 | 14 | 12.88% | 9.32% | 9.295% | 9.231% | 9.32% | 9.231% | 12.88% | 12.89% | 12.88% | 12.88% | 9.295% | 9.32%
180 | 15 | 11.58% | 9.072% | 9.068% | 9.146% | 8.93% | 9.146% | 11.3% | 11.3% | 11.58% | 11.58% | 9.068% | 8.93%
180 | 16 | 11.31% | 9.781% | 9.852% | 9.805% | 9.845% | 9.805% | 11.69% | 11.69% | 11.31% | 11.31% | 9.852% | 9.845%
180 | 17 | 11.79% | 9.882% | 9.783% | 9.882% | 9.882% | 9.882% | 11.79% | 11.81% | 11.79% | 11.79% | 9.783% | 9.882%
180 | 18 | 11.19% | 9.27% | 9.341% | 9.27% | 9.27% | 9.27% | 11.19% | 11.25% | 11.19% | 11.19% | 9.341% | 9.27%
180 | 19 | 11.71% | 9.741% | 9.44% | 9.44% | 9.741% | 9.44% | 11.71% | 11.68% | 11.71% | 11.71% | 9.44% | 9.741%
180 | 20 | 10.36% | 9.053% | 9.48% | 9.48% | 9.053% | 9.48% | 10.36% | 10.52% | 10.36% | 10.36% | 9.48% | 9.053%
180 | 21 | 11.01% | 10.07% | 9.512% | 9.512% | 9.512% | 9.512% | 11.01% | 11.01% | 11.01% | 11.01% | 9.512% | 9.512%
180 | 22 | 10.86% | 9.856% | 10.29% | 10.29% | 10.29% | 10.29% | 10.73% | 10.73% | 10.86% | 10.86% | 10.29% | 10.29%
180 | 23 | 12.29% | 8.129% | 8.333% | 8.129% | 8.129% | 8.129% | 12.11% | 12.11% | 12.29% | 12.29% | 8.333% | 8.129%
180 | 24 | 11.29% | 7.212% | 7.466% | 7.212% | 7.212% | 7.212% | 11.29% | 11.84% | 11.29% | 11.29% | 7.466% | 7.212%
180 | 25 | 8.908% | 8.224% | 8.224% | 8.224% | 8.224% | 8.224% | 8.908% | 8.957% | 8.908% | 8.908% | 8.224% | 8.224%
180 | 26 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
180 | 27 | 22.36% | 0% | 0% | 0% | 0% | 0% | 22.36% | 22.36% | 22.36% | 22.36% | 0% | 0%
180 | 28 | 9.924% | 0% | 0% | 0% | 0% | 0% | 9.924% | 9.924% | 9.924% | 9.924% | 0% | 0%
180 | 29 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
180 | 30 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
180 | 31 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
180 | 32 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
180 | 33 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
180 | 34 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
180 | 35 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
180 | 36 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
180 | 37 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
180 | 38 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
180 | 39 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
180 | 40 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
210 | 0 | 67.16% | 50% | 50% | 50% | 50% | 50% | 67.16% | 67.16% | 67.16% | 67.16% | 50% | 50%
210 | 1 | 70.87% | 65.21% | 65.21% | 65.21% | 65.21% | 65.21% | 70.87% | 70.87% | 70.87% | 70.87% | 65.21% | 65.21%
210 | 2 | 51.98% | 51.77% | 52.93% | 51.77% | 51.77% | 51.77% | 51.98% | 51.98% | 51.98% | 51.98% | 52.93% | 51.77%
210 | 3 | 36.28% | 36.98% | 37.39% | 37.22% | 36.98% | 37.22% | 36.28% | 36.89% | 36.28% | 36.28% | 37.39% | 36.98%
210 | 4 | 27.76% | 27.81% | 27.74% | 27.74% | 27.81% | 27.74% | 27.76% | 27.66% | 27.76% | 27.76% | 27.74% | 27.81%
210 | 5 | 22.41% | 22.81% | 22.81% | 22.81% | 22.81% | 22.81% | 22.41% | 22.41% | 22.41% | 22.41% | 22.81% | 22.81%
210 | 6 | 16.69% | 19.18% | 19.18% | 19.18% | 19.18% | 19.18% | 16.69% | 16.76% | 16.69% | 16.69% | 19.18% | 19.18%
210 | 7 | 13.79% | 15.85% | 15.82% | 15.85% | 15.85% | 15.85% | 13.79% | 13.76% | 13.79% | 13.79% | 15.82% | 15.85%
210 | 8 | 12.15% | 14.91% | 15.48% | 15.44% | 14.91% | 15.44% | 12.17% | 12.17% | 12.15% | 12.15% | 15.48% | 14.91%
210 | 9 | 10.8% | 14.03% | 13.72% | 13.72% | 14.03% | 13.72% | 10.79% | 10.79% | 10.8% | 10.8% | 13.72% | 14.03%
210 | 10 | 11.21% | 12.58% | 12.51% | 12.48% | 12.58% | 12.48% | 11.21% | 11.15% | 11.21% | 11.21% | 12.51% | 12.58%
210 | 11 | 10.25% | 10.7% | 10.78% | 10.79% | 10.73% | 10.79% | 10.25% | 10.49% | 10.25% | 10.25% | 10.78% | 10.73%
210 | 12 | 11.64% | 9.428% | 9.416% | 9.413% | 9.413% | 9.413% | 11.64% | 11.64% | 11.64% | 11.64% | 9.416% | 9.413%
210 | 13 | 12.42% | 8.673% | 8.742% | 8.685% | 8.673% | 8.685% | 12.42% | 12.42% | 12.42% | 12.42% | 8.742% | 8.673%
210 | 14 | 14.35% | 8.857% | 8.755% | 8.84% | 8.857% | 8.84% | 14.35% | 14.35% | 14.35% | 14.35% | 8.755% | 8.857%
210 | 15 | 15.71% | 9.178% | 9.256% | 9.256% | 9.312% | 9.256% | 15.71% | 15.71% | 15.71% | 15.71% | 9.256% | 9.312%
210 | 16 | 11.82% | 9.204% | 9.061% | 9.061% | 9.061% | 9.061% | 11.82% | 11.82% | 11.82% | 11.82% | 9.061% | 9.061%
210 | 17 | 20.07% | 11.17% | 11.35% | 10.73% | 10.73% | 10.73% | 20.07% | 22.75% | 20.07% | 20.07% | 11.35% | 10.73%
210 | 18 | 10.83% | 10.1% | 9.054% | 10.1% | 10.1% | 10.1% | 10.83% | 10.68% | 10.83% | 10.83% | 9.054% | 10.1%
210 | 19 | 11.31% | 14.39% | 16.34% | 14.39% | 14.39% | 14.39% | 11.31% | 11.31% | 11.31% | 11.31% | 16.34% | 14.39%
210 | 20 | 11.12% | 9.924% | 9.924% | 9.924% | 9.924% | 9.924% | 11.12% | 11.12% | 11.12% | 11.12% | 9.924% | 9.924%
210 | 21 | 11.19% | 0% | 0% | 0% | 0% | 0% | 11.19% | 11.19% | 11.19% | 11.19% | 0% | 0%
210 | 22 | 0% | 9.753% | 9.753% | 9.753% | 9.753% | 9.753% | 0% | 0% | 0% | 0% | 9.753% | 9.753%
210 | 23 | 0% | 9.901% | 9.901% | 9.901% | 9.901% | 9.901% | 0% | 0% | 0% | 0% | 9.901% | 9.901%
210 | 24 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
210 | 25 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
210 | 26 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
210 | 27 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
210 | 28 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
210 | 29 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
210 | 30 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
210 | 31 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
210 | 32 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
210 | 33 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
210 | 34 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
210 | 35 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
210 | 36 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
210 | 37 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
210 | 38 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
210 | 39 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
210 | 40 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
240 | 0 | 50% | 205.8% | 205.8% | 205.8% | 205.8% | 205.8% | 50% | 50% | 50% | 50% | 205.8% | 205.8%
240 | 1 | 81.49% | 67.95% | 67.95% | 67.95% | 67.95% | 67.95% | 81.49% | 81.49% | 81.49% | 81.49% | 67.95% | 67.95%
240 | 2 | 49.3% | 46.54% | 48.02% | 46.54% | 46.54% | 46.54% | 49.3% | 49.3% | 49.3% | 49.3% | 48.02% | 46.54%
240 | 3 | 35.39% | 37.29% | 37.34% | 37.29% | 37.29% | 37.29% | 35.39% | 35.05% | 35.39% | 35.39% | 37.34% | 37.29%
240 | 4 | 28.44% | 27.28% | 27.28% | 27.28% | 27.28% | 27.28% | 28.44% | 29.21% | 28.44% | 28.44% | 27.28% | 27.28%
240 | 5 | 23.46% | 23.77% | 23.77% | 23.77% | 23.77% | 23.77% | 23.46% | 23.46% | 23.46% | 23.46% | 23.77% | 23.77%
240 | 6 | 17.54% | 18.18% | 17.91% | 17.91% | 17.91% | 17.91% | 17.54% | 17.54% | 17.54% | 17.54% | 17.91% | 17.91%
240 | 7 | 15.47% | 16% | 16.22% | 16.22% | 16.22% | 16.22% | 15.47% | 15.47% | 15.47% | 15.47% | 16.22% | 16.22%
240 | 8 | 13.76% | 14.88% | 15.06% | 15.01% | 14.88% | 15.01% | 13.76% | 13.76% | 13.76% | 13.76% | 15.06% | 14.88%
240 | 9 | 12.83% | 12.03% | 12.06% | 12.08% | 12.03% | 12.08% | 12.83% | 12.83% | 12.83% | 12.83% | 12.06% | 12.03%
240 | 10 | 11.27% | 10.97% | 10.92% | 10.97% | 10.97% | 10.97% | 11.27% | 11.23% | 11.27% | 11.27% | 10.92% | 10.97%
240 | 11 | 10.61% | 10.72% | 10.77% | 10.72% | 10.72% | 10.72% | 10.61% | 10.73% | 10.61% | 10.61% | 10.77% | 10.72%
240 | 12 | 9.527% | 9.663% | 9.663% | 9.663% | 9.663% | 9.663% | 9.527% | 9.527% | 9.527% | 9.527% | 9.663% | 9.663%
240 | 13 | 10.98% | 8.479% | 8.53% | 8.479% | 8.479% | 8.479% | 10.98% | 10.87% | 10.98% | 10.98% | 8.53% | 8.479%
240 | 14 | 10.19% | 9.452% | 9.306% | 9.452% | 9.452% | 9.452% | 10.19% | 10.41% | 10.19% | 10.19% | 9.306% | 9.452%
240 | 15 | 10.55% | 9.867% | 9.922% | 9.922% | 9.922% | 9.922% | 11.06% | 11.06% | 10.55% | 10.55% | 9.922% | 9.922%
240 | 16 | 11.93% | 9.149% | 9.114% | 9.114% | 9.114% | 9.114% | 11.32% | 11.32% | 11.93% | 11.93% | 9.114% | 9.114%
240 | 17 | 13.2% | 12.93% | 12.93% | 12.93% | 12.93% | 12.93% | 13.2% | 13.2% | 13.2% | 13.2% | 12.93% | 12.93%
240 | 18 | 12.9% | 10.25% | 10.25% | 10.25% | 10.25% | 10.25% | 12.9% | 12.9% | 12.9% | 12.9% | 10.25% | 10.25%
240 | 19 | 11.49% | 10.69% | 10.69% | 10.69% | 10.69% | 10.69% | 11.49% | 10.64% | 11.49% | 11.49% | 10.69% | 10.69%
240 | 20 | 11.71% | 9.914% | 9.914% | 9.914% | 9.914% | 9.914% | 11.71% | 12% | 11.71% | 11.71% | 9.914% | 9.914%
240 | 21 | 13.66% | 10.01% | 10.81% | 10.81% | 10.81% | 10.81% | 13.66% | 13.66% | 13.66% | 13.66% | 10.81% | 10.81%
240 | 22 | 10.91% | 11.12% | 9.764% | 9.764% | 9.764% | 9.764% | 10.91% | 10.91% | 10.91% | 10.91% | 9.764% | 9.764%
240 | 23 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
240 | 24 | 10.84% | 0% | 0% | 0% | 0% | 0% | 10.84% | 10.84% | 10.84% | 10.84% | 0% | 0%
240 | 25 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
240 | 26 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
240 | 27 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
240 | 28 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
240 | 29 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
240 | 30 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
240 | 31 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
240 | 32 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
240 | 33 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
240 | 34 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
240 | 35 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
240 | 36 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
240 | 37 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
240 | 38 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
240 | 39 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
240 | 40 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
270 | 0 | 35.4% | 0% | 0% | 0% | 0% | 0% | 35.4% | 35.4% | 35.4% | 35.4% | 0% | 0%
270 | 1 | 68.01% | 59.63% | 59.63% | 59.63% | 59.63% | 59.63% | 68.01% | 68.01% | 68.01% | 68.01% | 59.63% | 59.63%
270 | 2 | 42.11% | 42.77% | 43.34% | 42.57% | 42.57% | 42.57% | 42.11% | 42.11% | 42.11% | 42.11% | 43.34% | 42.57%
270 | 3 | 32.33% | 31.91% | 32.24% | 32.11% | 32.11% | 32.11% | 32.33% | 32.31% | 32.33% | 32.33% | 32.24% | 32.11%
270 | 4 | 25.79% | 24.5% | 24.5% | 24.5% | 24.5% | 24.5% | 25.79% | 25.87% | 25.79% | 25.79% | 24.5% | 24.5%
270 | 5 | 21.44% | 21.27% | 21.27% | 21.27% | 21.27% | 21.27% | 21.44% | 21.44% | 21.44% | 21.44% | 21.27% | 21.27%
270 | 6 | 19.3% | 16.38% | 16.44% | 16.43% | 16.43% | 16.43% | 19.3% | 19.34% | 19.3% | 19.3% | 16.44% | 16.43%
270 | 7 | 17.28% | 14.27% | 14.23% | 14.24% | 14.24% | 14.24% | 17.28% | 17.25% | 17.28% | 17.28% | 14.23% | 14.24%
270 | 8 | 13.12% | 12.17% | 12.32% | 12.28% | 12.16% | 12.28% | 13.1% | 13.1% | 13.12% | 13.12% | 12.32% | 12.16%
270 | 9 | 13.69% | 10.66% | 10.64% | 10.65% | 10.68% | 10.65% | 13.72% | 13.72% | 13.69% | 13.69% | 10.64% | 10.68%
270 | 10 | 12.88% | 9.997% | 10.08% | 10.06% | 9.997% | 10.06% | 12.88% | 12.94% | 12.88% | 12.88% | 10.08% | 9.997%
270 | 11 | 11.08% | 9.732% | 9.799% | 9.758% | 9.776% | 9.758% | 11.08% | 11.22% | 11.08% | 11.08% | 9.799% | 9.776%
270 | 12 | 11.2% | 9.833% | 9.728% | 9.778% | 9.778% | 9.778% | 11.2% | 11.2% | 11.2% | 11.2% | 9.728% | 9.778%
270 | 13 | 10.99% | 9.354% | 9.463% | 9.354% | 9.354% | 9.354% | 10.99% | 10.8% | 10.99% | 10.99% | 9.463% | 9.354%
270 | 14 | 11.65% | 9.964% | 9.579% | 9.849% | 9.964% | 9.849% | 11.65% | 11.89% | 11.65% | 11.65% | 9.579% | 9.964%
270 | 15 | 9.274% | 10.01% | 10.36% | 10.36% | 10.28% | 10.36% | 9.078% | 9.07% | 9.274% | 9.274% | 10.36% | 10.28%
270 | 16 | 9.199% | 9.163% | 8.984% | 8.984% | 8.984% | 8.984% | 9.552% | 9.382% | 9.199% | 9.199% | 8.984% | 8.984%
270 | 17 | 10.9% | 13.19% | 13.34% | 13.19% | 13.19% | 13.19% | 10.9% | 11.4% | 10.9% | 10.9% | 13.34% | 13.19%
270 | 18 | 9.87% | 10.19% | 10.36% | 10.19% | 10.19% | 10.19% | 9.87% | 9.554% | 9.87% | 9.87% | 10.36% | 10.19%
270 | 19 | 13.85% | 11.38% | 11.38% | 11.38% | 11.38% | 11.38% | 13.85% | 13.85% | 13.85% | 13.85% | 11.38% | 11.38%
270 | 20 | 12.89% | 10.68% | 10.89% | 10.89% | 10.68% | 10.89% | 12.89% | 12.89% | 12.89% | 12.89% | 10.89% | 10.68%
270 | 21 | 11.72% | 10.7% | 10.28% | 10.28% | 10.7% | 10.28% | 11.72% | 11.72% | 11.72% | 11.72% | 10.28% | 10.7%
270 | 22 | 12.36% | 14.5% | 14.5% | 14.5% | 14.5% | 14.5% | 12.36% | 12.36% | 12.36% | 12.36% | 14.5% | 14.5%
270 | 23 | 11.05% | 15.34% | 15.34% | 15.34% | 15.34% | 15.34% | 11.05% | 11.05% | 11.05% | 11.05% | 15.34% | 15.34%
270 | 24 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
270 | 25 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
270 | 26 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
270 | 27 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
270 | 28 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
270 | 29 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
270 | 30 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
270 | 31 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
270 | 32 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
270 | 33 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
270 | 34 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
270 | 35 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
270 | 36 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
270 | 37 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
270 | 38 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
270 | 39 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
270 | 40 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
300 | 0 | 74.44% | 240% | 240% | 240% | 240% | 240% | 74.44% | 74.44% | 74.44% | 74.44% | 240% | 240%
300 | 1 | 69.77% | 73.55% | 73.55% | 73.55% | 73.55% | 73.55% | 69.77% | 69.77% | 69.77% | 69.77% | 73.55% | 73.55%
300 | 2 | 49.07% | 44.3% | 45.66% | 44.3% | 44.3% | 44.3% | 49.07% | 48.48% | 49.07% | 49.07% | 45.66% | 44.3%
300 | 3 | 38.18% | 34.8% | 34.74% | 34.8% | 34.8% | 34.8% | 38.18% | 38.87% | 38.18% | 38.18% | 34.74% | 34.8%
300 | 4 | 27.5% | 25.29% | 25.32% | 25.29% | 25.29% | 25.29% | 27.42% | 27.87% | 27.5% | 27.5% | 25.32% | 25.29%
300 | 5 | 22.73% | 20.11% | 20.11% | 20.11% | 20.11% | 20.11% | 22.82% | 22.77% | 22.73% | 22.73% | 20.11% | 20.11%
300 | 6 | 18.43% | 17.02% | 16.98% | 16.98% | 16.98% | 16.98% | 18.43% | 18.39% | 18.43% | 18.43% | 16.98% | 16.98%
300 | 7 | 15.12% | 14.3% | 14.36% | 14.36% | 14.36% | 14.36% | 15.12% | 15.24% | 15.12% | 15.12% | 14.36% | 14.36%
300 | 8 | 14.43% | 12.88% | 13.07% | 13.07% | 12.86% | 13.07% | 14.42% | 14.42% | 14.43% | 14.43% | 13.07% | 12.86%
300 | 9 | 12.51% | 12.09% | 11.97% | 11.97% | 12.11% | 11.97% | 12.53% | 12.53% | 12.51% | 12.51% | 11.97% | 12.11%
300 | 10 | 11.2% | 11.13% | 11.01% | 10.99% | 11.13% | 10.99% | 11.2% | 11.21% | 11.2% | 11.2% | 11.01% | 11.13%
300 | 11 | 9.921% | 10.03% | 10.2% | 10.22% | 10.03% | 10.22% | 9.921% | 10.12% | 9.921% | 9.921% | 10.2% | 10.03%
300 | 12 | 10.14% | 9.291% | 9.345% | 9.291% | 9.291% | 9.291% | 10.14% | 10.14% | 10.14% | 10.14% | 9.345% | 9.291%
300 | 13 | 9.437% | 8.5% | 8.543% | 8.5% | 8.5% | 8.5% | 9.437% | 9.437% | 9.437% | 9.437% | 8.543% | 8.5%
300 | 14 | 8.653% | 10.61% | 9.829% | 10.08% | 10.61% | 10.08% | 8.653% | 8.653% | 8.653% | 8.653% | 9.829% | 10.61%
300 | 15 | 8.305% | 11.32% | 11.22% | 11.22% | 10.51% | 11.22% | 8.457% | 8.457% | 8.305% | 8.305% | 11.22% | 10.51%
300 | 16 | 12.14% | 11.63% | 12.43% | 12.44% | 12.44% | 12.44% | 11.74% | 11.74% | 12.14% | 12.14% | 12.43% | 12.44%
300 | 17 | 15.87% | 13.73% | 12.29% | 13.73% | 13.73% | 13.73% | 15.87% | 16.18% | 15.87% | 15.87% | 12.29% | 13.73%
300 | 18 | 11.16% | 13.92% | 14.77% | 13.92% | 13.92% | 13.92% | 11.16% | 11.56% | 11.16% | 11.16% | 14.77% | 13.92%
300 | 19 | 10.14% | 11.03% | 11.03% | 11.03% | 11.03% | 11.03% | 10.14% | 10.14% | 10.14% | 10.14% | 11.03% | 11.03%
300 | 20 | 13.34% | 9.995% | 9.995% | 9.995% | 9.995% | 9.995% | 13.34% | 13.34% | 13.34% | 13.34% | 9.995% | 9.995%
300 | 21 | 11.66% | 10.44% | 10.44% | 10.44% | 10.44% | 10.44% | 11.66% | 11.66% | 11.66% | 11.66% | 10.44% | 10.44%
300 | 22 | 8.753% | 9.518% | 9.518% | 9.518% | 9.518% | 9.518% | 8.737% | 8.737% | 8.753% | 8.753% | 9.518% | 9.518%
300 | 23 | 7.614% | 5.604% | 5.604% | 5.604% | 5.604% | 5.604% | 8.214% | 8.214% | 7.614% | 7.614% | 5.604% | 5.604%
300 | 24 | 21.47% | 7.684% | 7.684% | 7.684% | 7.684% | 7.684% | 21.47% | 21.47% | 21.47% | 21.47% | 7.684% | 7.684%
300 | 25 | 0% | 8.489% | 8.489% | 8.489% | 8.489% | 8.489% | 0% | 0% | 0% | 0% | 8.489% | 8.489%
300 | 26 | 0% | 9.739% | 9.739% | 9.739% | 9.739% | 9.739% | 0% | 0% | 0% | 0% | 9.739% | 9.739%
300 | 27 | 0% | 9.743% | 9.743% | 9.743% | 9.743% | 9.743% | 0% | 0% | 0% | 0% | 9.743% | 9.743%
300 | 28 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
300 | 29 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
300 | 30 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
300 | 31 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
300 | 32 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
300 | 33 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
300 | 34 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
300 | 35 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
300 | 36 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
300 | 37 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
300 | 38 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
300 | 39 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
300 | 40 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
330 | 0 | 25% | 50% | 50% | 50% | 50% | 50% | 25% | 25% | 25% | 25% | 50% | 50%
330 | 1 | 68.95% | 71.38% | 71.38% | 71.38% | 71.38% | 71.38% | 68.95% | 68.95% | 68.95% | 68.95% | 71.38% | 71.38%
330 | 2 | 49.81% | 50.96% | 52.04% | 50.96% | 50.96% | 50.96% | 49.81% | 49.81% | 49.81% | 49.81% | 52.04% | 50.96%
330 | 3 | 38.76% | 34.81% | 35.43% | 34.81% | 34.81% | 34.81% | 38.76% | 39.2% | 38.76% | 38.76% | 35.43% | 34.81%
330 | 4 | 28.78% | 26.41% | 26.41% | 26.41% | 26.41% | 26.41% | 28.73% | 28.99% | 28.78% | 28.78% | 26.41% | 26.41%
330 | 5 | 23.19% | 20.91% | 20.91% | 20.91% | 20.91% | 20.91% | 23.19% | 23.19% | 23.19% | 23.19% | 20.91% | 20.91%
330 | 6 | 19.17% | 16.72% | 16.77% | 16.73% | 16.73% | 16.73% | 19.28% | 19.28% | 19.17% | 19.17% | 16.77% | 16.73%
330 | 7 | 16.28% | 15.31% | 15.27% | 15.3% | 15.3% | 15.3% | 16.28% | 16.28% | 16.28% | 16.28% | 15.27% | 15.3%
330 | 8 | 15.1% | 13.12% | 13.25% | 13.25% | 13.13% | 13.25% | 15.1% | 15.1% | 15.1% | 15.1% | 13.25% | 13.13%
330 | 9 | 13.26% | 12.02% | 12.01% | 11.95% | 12.02% | 11.95% | 13.27% | 13.27% | 13.26% | 13.26% | 12.01% | 12.02%
330 | 10 | 12.08% | 11.35% | 11.3% | 11.36% | 11.35% | 11.36% | 12.08% | 12.17% | 12.08% | 12.08% | 11.3% | 11.35%
330 | 11 | 11.48% | 11.48% | 11.47% | 11.48% | 11.49% | 11.48% | 11.48% | 11.44% | 11.48% | 11.48% | 11.47% | 11.49%
330 | 12 | 11.91% | 11.57% | 11.48% | 11.49% | 11.49% | 11.49% | 11.91% | 11.9% | 11.91% | 11.91% | 11.48% | 11.49%
330 | 13 | 10.73% | 11.16% | 11.28% | 11.25% | 11.25% | 11.25% | 10.73% | 10.77% | 10.73% | 10.73% | 11.28% | 11.25%
330 | 14 | 12.42% | 11.3% | 11.32% | 11.35% | 11.3% | 11.35% | 12.42% | 12.42% | 12.42% | 12.42% | 11.32% | 11.3%
330 | 15 | 12.41% | 11.75% | 11.5% | 11.79% | 11.98% | 11.79% | 11.91% | 11.91% | 12.41% | 12.41% | 11.5% | 11.98%
330 | 16 | 12.06% | 14.3% | 14.11% | 14.02% | 14.02% | 14.02% | 12.62% | 12.62% | 12.06% | 12.06% | 14.11% | 14.02%
330 | 17 | 12.44% | 12.69% | 12.69% | 12.69% | 12.69% | 12.69% | 12.44% | 12.5% | 12.44% | 12.44% | 12.69% | 12.69%
330 | 18 | 11.71% | 11.54% | 9.629% | 11.54% | 11.54% | 11.54% | 11.71% | 11.83% | 11.71% | 11.71% | 9.629% | 11.54%
330 | 19 | 10.38% | 10.73% | 13.18% | 10.68% | 10.73% | 10.68% | 10.38% | 10.38% | 10.38% | 10.38% | 13.18% | 10.73%
330 | 20 | 10.4% | 9.865% | 10.01% | 10.01% | 9.865% | 10.01% | 10.4% | 10.4% | 10.4% | 10.4% | 10.01% | 9.865%
330 | 21 | 12.45% | 10.61% | 10.61% | 10.61% | 10.61% | 10.61% | 12.45% | 12.45% | 12.45% | 12.45% | 10.61% | 10.61%
330 | 22 | 10.98% | 9.237% | 9.237% | 9.237% | 9.237% | 9.237% | 9.432% | 9.432% | 10.98% | 10.98% | 9.237% | 9.237%
330 | 23 | 0% | 9.556% | 9.556% | 9.556% | 9.556% | 9.556% | 12.53% | 12.53% | 0% | 0% | 9.556% | 9.556%
330 | 24 | 7.723% | 4.355% | 4.355% | 4.355% | 4.355% | 4.355% | 7.723% | 7.779% | 7.723% | 7.723% | 4.355% | 4.355%
330 | 25 | 7.468% | 0% | 0% | 0% | 0% | 0% | 7.468% | 7.539% | 7.468% | 7.468% | 0% | 0%
330 | 26 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
330 | 27 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
330 | 28 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
330 | 29 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
330 | 30 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
330 | 31 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
330 | 32 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
330 | 33 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
330 | 34 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
330 | 35 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
330 | 36 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
330 | 37 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
330 | 38 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
330 | 39 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
330 | 40 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108

## SD TI
Standard Deviation of Turbulence Intensity (%) [σI]
|  | Measurement Device |  | Wind Turbine
Wind Direction (Midpoint) (°) | Wind Speed (Midpoint) (m/s) | Gobblers Knob West | Gobblers Knob East | 97 | 98 | 100 | 102 | 103 | 104 | 105 | 106 | 107 | 108
ALL | 0 | 60.14% | 111.1% | 111.1% | 111.1% | 111.1% | 111.1% | 60.14% | 60.14% | 60.14% | 60.14% | 111.1% | 111.1%
ALL | 1 | 19.01% | 33.51% | 33.58% | 33.51% | 33.51% | 33.51% | 19.05% | 19.05% | 19.05% | 19.05% | 33.58% | 33.51%
ALL | 2 | 15.92% | 20.93% | 21.23% | 20.95% | 20.95% | 20.95% | 15.85% | 15.89% | 15.85% | 15.85% | 21.23% | 20.95%
ALL | 3 | 13.42% | 14.72% | 14.84% | 14.72% | 14.72% | 14.72% | 13.53% | 13.56% | 13.53% | 13.53% | 14.84% | 14.72%
ALL | 4 | 11.49% | 11.47% | 11.46% | 11.46% | 11.47% | 11.46% | 11.65% | 11.65% | 11.65% | 11.65% | 11.46% | 11.47%
ALL | 5 | 10.19% | 9.982% | 9.977% | 9.983% | 9.983% | 9.983% | 10.35% | 10.34% | 10.34% | 10.34% | 9.977% | 9.983%
ALL | 6 | 8.596% | 8.275% | 8.27% | 8.259% | 8.258% | 8.259% | 8.556% | 8.556% | 8.556% | 8.556% | 8.27% | 8.258%
ALL | 7 | 7.473% | 6.986% | 7.017% | 7.017% | 7.015% | 7.017% | 7.487% | 7.489% | 7.488% | 7.488% | 7.017% | 7.015%
ALL | 8 | 6.263% | 6.556% | 6.657% | 6.655% | 6.561% | 6.655% | 6.366% | 6.367% | 6.368% | 6.368% | 6.657% | 6.561%
ALL | 9 | 6.656% | 5.984% | 5.906% | 5.904% | 5.982% | 5.904% | 6.774% | 6.77% | 6.65% | 6.65% | 5.906% | 5.982%
ALL | 10 | 5.355% | 5.727% | 5.676% | 5.69% | 5.723% | 5.69% | 5.328% | 5.33% | 5.374% | 5.374% | 5.676% | 5.723%
ALL | 11 | 5.07% | 4.809% | 4.881% | 4.86% | 4.812% | 4.86% | 5.064% | 4.775% | 5.062% | 5.062% | 4.881% | 4.812%
ALL | 12 | 4.606% | 4.575% | 4.574% | 4.572% | 4.572% | 4.572% | 4.645% | 5.045% | 4.651% | 4.651% | 4.574% | 4.572%
ALL | 13 | 4.757% | 4.279% | 4.333% | 4.285% | 4.279% | 4.285% | 4.698% | 4.76% | 4.695% | 4.695% | 4.333% | 4.279%
ALL | 14 | 5.531% | 4.302% | 4.119% | 4.19% | 4.302% | 4.19% | 5.63% | 5.504% | 5.643% | 5.643% | 4.119% | 4.302%
ALL | 15 | 4.441% | 4.133% | 4.082% | 4.07% | 3.822% | 4.07% | 4.519% | 3.995% | 4.519% | 4.519% | 4.082% | 3.822%
ALL | 16 | 4.245% | 4.33% | 4.659% | 4.656% | 4.661% | 4.656% | 3.442% | 4.385% | 3.446% | 3.446% | 4.659% | 4.661%
ALL | 17 | 5.488% | 4.376% | 4.339% | 4.339% | 4.35% | 4.339% | 6.182% | 6.124% | 6.148% | 6.148% | 4.339% | 4.35%
ALL | 18 | 2.822% | 4.131% | 3.679% | 4.15% | 4.131% | 4.15% | 2.787% | 3.695% | 2.811% | 2.811% | 3.679% | 4.131%
ALL | 19 | 2.063% | 2.362% | 3.745% | 2.436% | 2.362% | 2.436% | 2.054% | 2.101% | 2.054% | 2.054% | 3.745% | 2.362%
ALL | 20 | 2.932% | 1.942% | 1.907% | 1.907% | 1.942% | 1.907% | 2.923% | 2.8% | 2.923% | 2.923% | 1.907% | 1.942%
ALL | 21 | 2.838% | 1.657% | 1.549% | 1.549% | 1.53% | 1.549% | 2.776% | 2.961% | 2.776% | 2.776% | 1.549% | 1.53%
ALL | 22 | 1.548% | 4.891% | 4.6% | 4.6% | 4.6% | 4.6% | 1.913% | 1.944% | 1.913% | 1.913% | 4.6% | 4.6%
ALL | 23 | 3% | 2.694% | 2.822% | 2.694% | 2.694% | 2.694% | 2.346% | 2.346% | 2.346% | 2.346% | 2.822% | 2.694%
ALL | 24 | 3.954% | 1.801% | 1.609% | 1.801% | 1.801% | 1.801% | 4.34% | 4.34% | 4.34% | 4.34% | 1.609% | 1.801%
ALL | 25 | 0.722% | 0.4018% | 0.4018% | 0.4018% | 0.4018% | 0.4018% | 0.6803% | 0.6803% | 0.6803% | 0.6803% | 0.4018% | 0.4018%
ALL | 26 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
ALL | 27 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
ALL | 28 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
ALL | 29 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
ALL | 30 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
ALL | 31 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
ALL | 32 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
ALL | 33 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
ALL | 34 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
ALL | 35 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
ALL | 36 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
ALL | 37 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
ALL | 38 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
ALL | 39 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
ALL | 40 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
0 | 0 | 95.42% | 2.058% | 2.058% | 2.058% | 2.058% | 2.058% | 95.42% | 95.42% | 95.42% | 95.42% | 2.058% | 2.058%
0 | 1 | 12.95% | 16.13% | 16.13% | 16.13% | 16.13% | 16.13% | 12.95% | 12.95% | 12.95% | 12.95% | 16.13% | 16.13%
0 | 2 | 14.82% | 24.73% | 25.31% | 24.73% | 24.73% | 24.73% | 14.82% | 14.82% | 14.82% | 14.82% | 25.31% | 24.73%
0 | 3 | 12.13% | 12.9% | 13.54% | 12.9% | 12.9% | 12.9% | 12.13% | 12.29% | 12.13% | 12.13% | 13.54% | 12.9%
0 | 4 | 9.517% | 12.9% | 12.9% | 12.9% | 12.9% | 12.9% | 9.517% | 9.663% | 9.517% | 9.517% | 12.9% | 12.9%
0 | 5 | 8.933% | 8.149% | 8.149% | 8.149% | 8.149% | 8.149% | 8.933% | 8.933% | 8.933% | 8.933% | 8.149% | 8.149%
0 | 6 | 8.702% | 7.155% | 7.155% | 7.155% | 7.155% | 7.155% | 8.702% | 8.767% | 8.702% | 8.702% | 7.155% | 7.155%
0 | 7 | 7.42% | 6.551% | 6.518% | 6.518% | 6.518% | 6.518% | 7.42% | 7.367% | 7.42% | 7.42% | 6.518% | 6.518%
0 | 8 | 6.02% | 5.614% | 5.624% | 5.624% | 5.624% | 5.624% | 6.02% | 6.02% | 6.02% | 6.02% | 5.624% | 5.624%
0 | 9 | 5.296% | 6.67% | 6.674% | 6.674% | 6.67% | 6.674% | 5.296% | 5.296% | 5.296% | 5.296% | 6.674% | 6.67%
0 | 10 | 5.669% | 6.405% | 6.367% | 6.367% | 6.405% | 6.367% | 5.669% | 5.991% | 5.669% | 5.669% | 6.367% | 6.405%
0 | 11 | 4.607% | 4.652% | 4.652% | 4.652% | 4.652% | 4.652% | 4.607% | 4.461% | 4.607% | 4.607% | 4.652% | 4.652%
0 | 12 | 5.035% | 3.077% | 3.092% | 3.077% | 3.077% | 3.077% | 5.035% | 5.035% | 5.035% | 5.035% | 3.092% | 3.077%
0 | 13 | 2.84% | 2.635% | 2.462% | 2.635% | 2.635% | 2.635% | 2.84% | 2.84% | 2.84% | 2.84% | 2.462% | 2.635%
0 | 14 | 2.578% | 4.244% | 4.282% | 4.285% | 4.244% | 4.285% | 2.578% | 2.578% | 2.578% | 2.578% | 4.282% | 4.244%
0 | 15 | 2.266% | 4.433% | 4.389% | 4.389% | 4.478% | 4.389% | 2.216% | 2.216% | 2.266% | 2.266% | 4.389% | 4.478%
0 | 16 | 1.926% | 8.789% | 8.393% | 8.393% | 8.393% | 8.393% | 2.08% | 2.08% | 1.926% | 1.926% | 8.393% | 8.393%
0 | 17 | 11.63% | 2.78% | 3.035% | 2.78% | 2.78% | 2.78% | 11.63% | 11.63% | 11.63% | 11.63% | 3.035% | 2.78%
0 | 18 | 1.829% | 1.351% | 1.314% | 1.351% | 1.351% | 1.351% | 1.829% | 1.829% | 1.829% | 1.829% | 1.314% | 1.351%
0 | 19 | 1.215% | 0% | 0% | 0% | 0% | 0% | 1.302% | 1.302% | 1.215% | 1.215% | 0% | 0%
0 | 20 | 3.529% | 2.479% | 2.479% | 2.479% | 2.479% | 2.479% | 3.743% | 3.743% | 3.529% | 3.529% | 2.479% | 2.479%
0 | 21 | 0% | 2.03% | 2.03% | 2.03% | 2.03% | 2.03% | 0% | 0% | 0% | 0% | 2.03% | 2.03%
0 | 22 | 1.698% | 0% | 0% | 0% | 0% | 0% | 1.698% | 1.698% | 1.698% | 1.698% | 0% | 0%
0 | 23 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
0 | 24 | 0.5649% | 0% | 0% | 0% | 0% | 0% | 0.5649% | 0.5649% | 0.5649% | 0.5649% | 0% | 0%
0 | 25 | 0.5778% | 0% | 0% | 0% | 0% | 0% | 0.5778% | 0.5778% | 0.5778% | 0.5778% | 0% | 0%
0 | 26 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
0 | 27 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
0 | 28 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
0 | 29 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
0 | 30 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
0 | 31 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
0 | 32 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
0 | 33 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
0 | 34 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
0 | 35 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
0 | 36 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
0 | 37 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
0 | 38 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
0 | 39 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
0 | 40 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
30 | 0 | 15.77% | 0% | 0% | 0% | 0% | 0% | 15.77% | 15.77% | 15.77% | 15.77% | 0% | 0%
30 | 1 | 20.98% | 28.24% | 28.24% | 28.24% | 28.24% | 28.24% | 20.98% | 20.98% | 20.98% | 20.98% | 28.24% | 28.24%
30 | 2 | 15.21% | 15.71% | 15.55% | 15.71% | 15.71% | 15.71% | 15.21% | 15.21% | 15.21% | 15.21% | 15.55% | 15.71%
30 | 3 | 11.32% | 14.1% | 14.52% | 14.1% | 14.1% | 14.1% | 11.32% | 11.16% | 11.32% | 11.32% | 14.52% | 14.1%
30 | 4 | 9.889% | 9.842% | 9.842% | 9.842% | 9.842% | 9.842% | 9.889% | 10.53% | 9.889% | 9.889% | 9.842% | 9.842%
30 | 5 | 10.2% | 8.393% | 8.393% | 8.393% | 8.393% | 8.393% | 10.2% | 10.2% | 10.2% | 10.2% | 8.393% | 8.393%
30 | 6 | 9.268% | 8.383% | 8.42% | 8.4% | 8.4% | 8.4% | 9.268% | 9.268% | 9.268% | 9.268% | 8.42% | 8.4%
30 | 7 | 6.829% | 7.645% | 7.521% | 7.555% | 7.612% | 7.555% | 6.829% | 6.829% | 6.829% | 6.829% | 7.521% | 7.612%
30 | 8 | 7.556% | 8.266% | 8.444% | 8.444% | 8.266% | 8.444% | 7.58% | 7.58% | 7.556% | 7.556% | 8.444% | 8.266%
30 | 9 | 8.493% | 5.155% | 5.314% | 5.314% | 5.155% | 5.314% | 8.457% | 8.457% | 8.493% | 8.493% | 5.314% | 5.155%
30 | 10 | 5.932% | 7.305% | 7.389% | 7.391% | 7.305% | 7.391% | 5.932% | 6.13% | 5.932% | 5.932% | 7.389% | 7.305%
30 | 11 | 8.95% | 5.032% | 4.998% | 4.972% | 5.032% | 4.972% | 8.95% | 8.398% | 8.95% | 8.95% | 4.998% | 5.032%
30 | 12 | 3.32% | 6.474% | 6.481% | 6.523% | 6.523% | 6.523% | 3.32% | 3.32% | 3.32% | 3.32% | 6.481% | 6.523%
30 | 13 | 9.244% | 4.828% | 4.778% | 4.754% | 4.754% | 4.754% | 9.244% | 9.244% | 9.244% | 9.244% | 4.778% | 4.754%
30 | 14 | 5.187% | 4.169% | 3.851% | 4.173% | 4.169% | 4.173% | 5.187% | 5.187% | 5.187% | 5.187% | 3.851% | 4.169%
30 | 15 | 8.99% | 7.667% | 4.814% | 3.889% | 4.019% | 3.889% | 8.99% | 8.99% | 8.99% | 8.99% | 4.814% | 4.019%
30 | 16 | 5.205% | 1.785% | 8.168% | 8.563% | 8.563% | 8.563% | 5.205% | 5.205% | 5.205% | 5.205% | 8.168% | 8.563%
30 | 17 | 1.584% | 5.824% | 4.591% | 4.591% | 5.326% | 4.591% | 1.584% | 1.584% | 1.584% | 1.584% | 4.591% | 5.326%
30 | 18 | 0% | 2.898% | 4.186% | 4.186% | 2.898% | 4.186% | 0% | 0% | 0% | 0% | 4.186% | 2.898%
30 | 19 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
30 | 20 | 0% | 0.6409% | 0.6409% | 0.6409% | 0.6409% | 0.6409% | 0% | 0% | 0% | 0% | 0.6409% | 0.6409%
30 | 21 | 0.7239% | 0.5861% | 0.5861% | 0.5861% | 0.5861% | 0.5861% | 0.7239% | 0.7239% | 0.7239% | 0.7239% | 0.5861% | 0.5861%
30 | 22 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
30 | 23 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
30 | 24 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
30 | 25 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
30 | 26 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
30 | 27 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
30 | 28 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
30 | 29 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
30 | 30 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
30 | 31 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
30 | 32 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
30 | 33 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
30 | 34 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
30 | 35 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
30 | 36 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
30 | 37 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
30 | 38 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
30 | 39 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
30 | 40 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
60 | 0 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
60 | 1 | 10.67% | 29.03% | 29.03% | 29.03% | 29.03% | 29.03% | 10.67% | 10.67% | 10.67% | 10.67% | 29.03% | 29.03%
60 | 2 | 12.7% | 31.2% | 31.05% | 31.2% | 31.2% | 31.2% | 12.7% | 12.7% | 12.7% | 12.7% | 31.05% | 31.2%
60 | 3 | 14.11% | 18.18% | 17.99% | 18.18% | 18.18% | 18.18% | 14.11% | 14.09% | 14.11% | 14.11% | 17.99% | 18.18%
60 | 4 | 11.6% | 9.266% | 9.266% | 9.266% | 9.266% | 9.266% | 11.6% | 11.46% | 11.6% | 11.6% | 9.266% | 9.266%
60 | 5 | 9.777% | 11.7% | 11.7% | 11.7% | 11.7% | 11.7% | 9.776% | 9.356% | 9.777% | 9.777% | 11.7% | 11.7%
60 | 6 | 10.88% | 9.294% | 9.294% | 9.294% | 9.294% | 9.294% | 10.83% | 11.35% | 10.88% | 10.88% | 9.294% | 9.294%
60 | 7 | 8.489% | 7.174% | 7.174% | 7.174% | 7.174% | 7.174% | 8.489% | 8.489% | 8.489% | 8.489% | 7.174% | 7.174%
60 | 8 | 6.391% | 4.576% | 4.636% | 4.636% | 4.584% | 4.636% | 6.391% | 6.391% | 6.391% | 6.391% | 4.636% | 4.584%
60 | 9 | 8.451% | 6.616% | 6.372% | 6.372% | 6.589% | 6.372% | 8.451% | 8.451% | 8.451% | 8.451% | 6.372% | 6.589%
60 | 10 | 4.869% | 7.393% | 7.393% | 7.393% | 7.393% | 7.393% | 4.869% | 5.017% | 4.869% | 4.869% | 7.393% | 7.393%
60 | 11 | 4.734% | 4.656% | 4.656% | 4.656% | 4.656% | 4.656% | 4.734% | 4.565% | 4.734% | 4.734% | 4.656% | 4.656%
60 | 12 | 6.485% | 3.636% | 3.675% | 3.636% | 3.636% | 3.636% | 6.485% | 6.485% | 6.485% | 6.485% | 3.675% | 3.636%
60 | 13 | 4.156% | 2.199% | 2.305% | 2.199% | 2.199% | 2.199% | 4.156% | 4.156% | 4.156% | 4.156% | 2.305% | 2.199%
60 | 14 | 5.194% | 4.463% | 4.323% | 4.613% | 4.463% | 4.613% | 5.194% | 5.194% | 5.194% | 5.194% | 4.323% | 4.463%
60 | 15 | 2.054% | 3.437% | 3.241% | 3.241% | 3.437% | 3.241% | 2.054% | 2.054% | 2.054% | 2.054% | 3.241% | 3.437%
60 | 16 | 1.149% | 2.535% | 2.535% | 2.535% | 2.535% | 2.535% | 1.149% | 1.149% | 1.149% | 1.149% | 2.535% | 2.535%
60 | 17 | 0% | 13.44% | 13.44% | 13.44% | 13.44% | 13.44% | 0% | 0% | 0% | 0% | 13.44% | 13.44%
60 | 18 | 0% | 3.352% | 3.352% | 3.352% | 3.352% | 3.352% | 0% | 0% | 0% | 0% | 3.352% | 3.352%
60 | 19 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
60 | 20 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
60 | 21 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
60 | 22 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
60 | 23 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
60 | 24 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
60 | 25 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
60 | 26 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
60 | 27 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
60 | 28 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
60 | 29 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
60 | 30 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
60 | 31 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
60 | 32 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
60 | 33 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
60 | 34 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
60 | 35 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
60 | 36 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
60 | 37 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
60 | 38 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
60 | 39 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
60 | 40 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
90 | 0 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
90 | 1 | 11.82% | 69.81% | 69.81% | 69.81% | 69.81% | 69.81% | 11.82% | 11.82% | 11.82% | 11.82% | 69.81% | 69.81%
90 | 2 | 14.6% | 12.66% | 12.95% | 12.66% | 12.66% | 12.66% | 14.6% | 14.6% | 14.6% | 14.6% | 12.95% | 12.66%
90 | 3 | 11.73% | 11.07% | 10.97% | 11.07% | 11.07% | 11.07% | 11.73% | 11.13% | 11.73% | 11.73% | 10.97% | 11.07%
90 | 4 | 12.82% | 11.34% | 11.29% | 11.34% | 11.34% | 11.34% | 12.82% | 13.23% | 12.82% | 12.82% | 11.29% | 11.34%
90 | 5 | 8.481% | 10% | 10% | 10% | 10% | 10% | 8.481% | 8.481% | 8.481% | 8.481% | 10% | 10%
90 | 6 | 6.374% | 7.926% | 7.914% | 7.926% | 7.926% | 7.926% | 6.374% | 6.374% | 6.374% | 6.374% | 7.914% | 7.926%
90 | 7 | 7.728% | 5.4% | 5.4% | 5.4% | 5.4% | 5.4% | 7.728% | 7.728% | 7.728% | 7.728% | 5.4% | 5.4%
90 | 8 | 6.023% | 9.17% | 9.269% | 9.269% | 9.163% | 9.269% | 6.023% | 6.023% | 6.023% | 6.023% | 9.269% | 9.163%
90 | 9 | 5.301% | 4.878% | 4.82% | 4.82% | 4.912% | 4.82% | 5.301% | 5.301% | 5.301% | 5.301% | 4.82% | 4.912%
90 | 10 | 4.646% | 4.395% | 4.395% | 4.395% | 4.395% | 4.395% | 4.646% | 4.717% | 4.646% | 4.646% | 4.395% | 4.395%
90 | 11 | 4.559% | 8.557% | 8.557% | 8.557% | 8.557% | 8.557% | 4.559% | 4.438% | 4.559% | 4.559% | 8.557% | 8.557%
90 | 12 | 5.436% | 6.738% | 6.738% | 6.738% | 6.738% | 6.738% | 5.436% | 5.436% | 5.436% | 5.436% | 6.738% | 6.738%
90 | 13 | 5.273% | 4.155% | 4.298% | 4.155% | 4.155% | 4.155% | 5.273% | 5.273% | 5.273% | 5.273% | 4.298% | 4.155%
90 | 14 | 4.317% | 10.51% | 9.978% | 10.51% | 10.51% | 10.51% | 4.317% | 4.317% | 4.317% | 4.317% | 9.978% | 10.51%
90 | 15 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
90 | 16 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
90 | 17 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
90 | 18 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
90 | 19 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
90 | 20 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
90 | 21 | 0% | 1.099% | 1.099% | 1.099% | 1.099% | 1.099% | 0% | 0% | 0% | 0% | 1.099% | 1.099%
90 | 22 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
90 | 23 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
90 | 24 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
90 | 25 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
90 | 26 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
90 | 27 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
90 | 28 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
90 | 29 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
90 | 30 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
90 | 31 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
90 | 32 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
90 | 33 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
90 | 34 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
90 | 35 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
90 | 36 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
90 | 37 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
90 | 38 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
90 | 39 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
90 | 40 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
120 | 0 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
120 | 1 | 15.04% | 32.1% | 32.24% | 32.1% | 32.1% | 32.1% | 15.04% | 15.04% | 15.04% | 15.04% | 32.24% | 32.1%
120 | 2 | 14.03% | 12.28% | 12.4% | 12.28% | 12.28% | 12.28% | 14.03% | 14.03% | 14.03% | 14.03% | 12.4% | 12.28%
120 | 3 | 12.33% | 16.36% | 16.3% | 16.36% | 16.36% | 16.36% | 12.33% | 12.66% | 12.33% | 12.33% | 16.3% | 16.36%
120 | 4 | 11.45% | 10.89% | 10.89% | 10.89% | 10.89% | 10.89% | 11.4% | 11.44% | 11.45% | 11.45% | 10.89% | 10.89%
120 | 5 | 10.42% | 10.07% | 10.07% | 10.07% | 10.07% | 10.07% | 10.53% | 10.53% | 10.42% | 10.42% | 10.07% | 10.07%
120 | 6 | 10.11% | 7.338% | 7.347% | 7.347% | 7.347% | 7.347% | 10.11% | 10.11% | 10.11% | 10.11% | 7.347% | 7.347%
120 | 7 | 8.386% | 6.256% | 6.233% | 6.233% | 6.233% | 6.233% | 8.386% | 8.386% | 8.386% | 8.386% | 6.233% | 6.233%
120 | 8 | 6.191% | 5.769% | 5.828% | 5.828% | 5.785% | 5.828% | 6.191% | 6.191% | 6.191% | 6.191% | 5.828% | 5.785%
120 | 9 | 6.628% | 4.592% | 4.587% | 4.587% | 4.601% | 4.587% | 6.628% | 6.628% | 6.628% | 6.628% | 4.587% | 4.601%
120 | 10 | 4.366% | 3.902% | 3.893% | 3.876% | 3.885% | 3.876% | 4.366% | 4.466% | 4.366% | 4.366% | 3.893% | 3.885%
120 | 11 | 3.408% | 3.433% | 3.417% | 3.433% | 3.433% | 3.433% | 3.408% | 3.449% | 3.408% | 3.408% | 3.417% | 3.433%
120 | 12 | 3.102% | 4.564% | 4.562% | 4.569% | 4.569% | 4.569% | 3.102% | 3.102% | 3.102% | 3.102% | 4.562% | 4.569%
120 | 13 | 3.111% | 4.609% | 4.637% | 4.612% | 4.613% | 4.612% | 3.111% | 3.111% | 3.111% | 3.111% | 4.637% | 4.613%
120 | 14 | 3.403% | 3.361% | 2.4% | 2.4% | 3.361% | 2.4% | 3.403% | 3.403% | 3.403% | 3.403% | 2.4% | 3.361%
120 | 15 | 2.728% | 3.711% | 4.887% | 4.887% | 4.05% | 4.887% | 2.728% | 2.728% | 2.728% | 2.728% | 4.887% | 4.05%
120 | 16 | 2.276% | 1.914% | 1.874% | 1.874% | 1.874% | 1.874% | 2.276% | 2.276% | 2.276% | 2.276% | 1.874% | 1.874%
120 | 17 | 1.323% | 0.439% | 0.4177% | 0.439% | 0.439% | 0.439% | 1.323% | 1.323% | 1.323% | 1.323% | 0.4177% | 0.439%
120 | 18 | 1.171% | 3.268% | 2.959% | 3.268% | 3.268% | 3.268% | 1.171% | 1.171% | 1.171% | 1.171% | 2.959% | 3.268%
120 | 19 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
120 | 20 | 0.4296% | 0% | 0% | 0% | 0% | 0% | 0.4296% | 0.4296% | 0.4296% | 0.4296% | 0% | 0%
120 | 21 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
120 | 22 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
120 | 23 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
120 | 24 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
120 | 25 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
120 | 26 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
120 | 27 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
120 | 28 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
120 | 29 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
120 | 30 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
120 | 31 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
120 | 32 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
120 | 33 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
120 | 34 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
120 | 35 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
120 | 36 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
120 | 37 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
120 | 38 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
120 | 39 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
120 | 40 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
150 | 0 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
150 | 1 | 41.41% | 19.98% | 19.98% | 19.98% | 19.98% | 19.98% | 41.41% | 41.41% | 41.41% | 41.41% | 19.98% | 19.98%
150 | 2 | 18.18% | 23.84% | 23.34% | 23.84% | 23.84% | 23.84% | 18.18% | 18.18% | 18.18% | 18.18% | 23.34% | 23.84%
150 | 3 | 14.3% | 13.64% | 15.44% | 13.64% | 13.64% | 13.64% | 14.3% | 14.64% | 14.3% | 14.3% | 15.44% | 13.64%
150 | 4 | 12.48% | 14.76% | 14.76% | 14.76% | 14.76% | 14.76% | 12.48% | 12.57% | 12.48% | 12.48% | 14.76% | 14.76%
150 | 5 | 9.929% | 8.892% | 8.896% | 8.896% | 8.896% | 8.896% | 9.929% | 9.929% | 9.929% | 9.929% | 8.896% | 8.896%
150 | 6 | 8.663% | 8.631% | 8.65% | 8.65% | 8.65% | 8.65% | 8.663% | 8.716% | 8.663% | 8.663% | 8.65% | 8.65%
150 | 7 | 8.367% | 7.013% | 7.013% | 7.013% | 7.013% | 7.013% | 8.367% | 8.33% | 8.367% | 8.367% | 7.013% | 7.013%
150 | 8 | 5.418% | 6.155% | 6.236% | 6.236% | 6.155% | 6.236% | 5.418% | 5.418% | 5.418% | 5.418% | 6.236% | 6.155%
150 | 9 | 6.633% | 5.808% | 5.741% | 5.741% | 5.808% | 5.741% | 6.633% | 6.633% | 6.633% | 6.633% | 5.741% | 5.808%
150 | 10 | 4.452% | 4.936% | 4.771% | 4.947% | 4.936% | 4.947% | 4.452% | 4.468% | 4.452% | 4.452% | 4.771% | 4.936%
150 | 11 | 3.666% | 4.319% | 4.535% | 4.308% | 4.319% | 4.308% | 3.666% | 3.787% | 3.666% | 3.666% | 4.535% | 4.319%
150 | 12 | 3.308% | 3.871% | 3.871% | 3.871% | 3.871% | 3.871% | 3.308% | 3.308% | 3.308% | 3.308% | 3.871% | 3.871%
150 | 13 | 3.774% | 2.615% | 2.702% | 2.624% | 2.615% | 2.624% | 3.774% | 3.785% | 3.774% | 3.774% | 2.702% | 2.615%
150 | 14 | 2.371% | 3.041% | 2.904% | 3.001% | 3.041% | 3.001% | 2.371% | 2.363% | 2.371% | 2.371% | 2.904% | 3.041%
150 | 15 | 2.427% | 2.915% | 2.885% | 2.867% | 2.798% | 2.867% | 2.449% | 2.449% | 2.427% | 2.427% | 2.885% | 2.798%
150 | 16 | 1.954% | 2.458% | 2.781% | 2.755% | 2.755% | 2.755% | 2.062% | 2.062% | 1.954% | 1.954% | 2.781% | 2.755%
150 | 17 | 1.965% | 3.121% | 3.102% | 3.065% | 3.065% | 3.065% | 1.994% | 2.081% | 1.965% | 1.965% | 3.102% | 3.065%
150 | 18 | 0.5826% | 2.257% | 2.376% | 2.348% | 2.257% | 2.348% | 0.6079% | 1.231% | 0.5826% | 0.5826% | 2.376% | 2.257%
150 | 19 | 1.797% | 2.146% | 1.99% | 1.99% | 2.146% | 1.99% | 1.797% | 1.511% | 1.797% | 1.797% | 1.99% | 2.146%
150 | 20 | 0.779% | 1.443% | 1.443% | 1.443% | 1.443% | 1.443% | 0.779% | 1.603% | 0.779% | 0.779% | 1.443% | 1.443%
150 | 21 | 1.865% | 0.8573% | 0.8573% | 0.8573% | 0.8573% | 0.8573% | 1.865% | 1.865% | 1.865% | 1.865% | 0.8573% | 0.8573%
150 | 22 | 1.027% | 0% | 0% | 0% | 0% | 0% | 1.237% | 1.237% | 1.027% | 1.027% | 0% | 0%
150 | 23 | 0% | 1.48% | 1.48% | 1.48% | 1.48% | 1.48% | 0% | 0% | 0% | 0% | 1.48% | 1.48%
150 | 24 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
150 | 25 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
150 | 26 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
150 | 27 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
150 | 28 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
150 | 29 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
150 | 30 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
150 | 31 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
150 | 32 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
150 | 33 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
150 | 34 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
150 | 35 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
150 | 36 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
150 | 37 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
150 | 38 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
150 | 39 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
150 | 40 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
180 | 0 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
180 | 1 | 17.78% | 39.64% | 39.64% | 39.64% | 39.64% | 39.64% | 17.78% | 17.78% | 17.78% | 17.78% | 39.64% | 39.64%
180 | 2 | 18.22% | 21.87% | 22.44% | 21.87% | 21.87% | 21.87% | 18.22% | 18.22% | 18.22% | 18.22% | 22.44% | 21.87%
180 | 3 | 16.1% | 15.74% | 15.6% | 15.74% | 15.74% | 15.74% | 16.1% | 16.38% | 16.1% | 16.1% | 15.6% | 15.74%
180 | 4 | 12.69% | 11.48% | 11.48% | 11.48% | 11.48% | 11.48% | 12.69% | 12.5% | 12.69% | 12.69% | 11.48% | 11.48%
180 | 5 | 12.23% | 12.54% | 12.55% | 12.54% | 12.54% | 12.54% | 12.23% | 12.23% | 12.23% | 12.23% | 12.55% | 12.54%
180 | 6 | 7.727% | 9.153% | 9.204% | 9.152% | 9.148% | 9.152% | 7.727% | 7.752% | 7.727% | 7.727% | 9.204% | 9.148%
180 | 7 | 6.833% | 6.7% | 6.682% | 6.682% | 6.678% | 6.682% | 6.833% | 6.821% | 6.833% | 6.833% | 6.682% | 6.678%
180 | 8 | 6.564% | 6.963% | 7.009% | 6.959% | 6.988% | 6.959% | 6.572% | 6.572% | 6.564% | 6.564% | 7.009% | 6.988%
180 | 9 | 4.907% | 5.827% | 5.889% | 5.901% | 5.836% | 5.901% | 4.902% | 4.902% | 4.907% | 4.907% | 5.889% | 5.836%
180 | 10 | 4.901% | 6.447% | 6.472% | 6.446% | 6.434% | 6.446% | 4.901% | 5.052% | 4.901% | 4.901% | 6.472% | 6.434%
180 | 11 | 4.441% | 4.848% | 4.823% | 4.84% | 4.848% | 4.84% | 4.441% | 4.309% | 4.441% | 4.441% | 4.823% | 4.848%
180 | 12 | 4.299% | 3.729% | 3.737% | 3.729% | 3.729% | 3.729% | 4.299% | 4.299% | 4.299% | 4.299% | 3.737% | 3.729%
180 | 13 | 4.46% | 4.562% | 4.619% | 4.572% | 4.562% | 4.572% | 4.46% | 4.476% | 4.46% | 4.46% | 4.619% | 4.562%
180 | 14 | 5.657% | 3.395% | 3.367% | 3.413% | 3.395% | 3.413% | 5.657% | 5.631% | 5.657% | 5.657% | 3.367% | 3.395%
180 | 15 | 2.662% | 2.642% | 2.739% | 2.695% | 2.529% | 2.695% | 2.525% | 2.525% | 2.662% | 2.662% | 2.739% | 2.529%
180 | 16 | 2.132% | 3.996% | 3.862% | 3.855% | 3.868% | 3.855% | 2.399% | 2.399% | 2.132% | 2.132% | 3.862% | 3.868%
180 | 17 | 2.231% | 2.247% | 2.307% | 2.247% | 2.247% | 2.247% | 2.231% | 2.339% | 2.231% | 2.231% | 2.307% | 2.247%
180 | 18 | 3.078% | 1.524% | 1.591% | 1.524% | 1.524% | 1.524% | 3.078% | 2.844% | 3.078% | 3.078% | 1.591% | 1.524%
180 | 19 | 1.869% | 1.318% | 1.261% | 1.261% | 1.318% | 1.261% | 1.869% | 1.9% | 1.869% | 1.869% | 1.261% | 1.318%
180 | 20 | 2.52% | 1.155% | 1.341% | 1.341% | 1.155% | 1.341% | 2.52% | 2.492% | 2.52% | 2.52% | 1.341% | 1.155%
180 | 21 | 1.283% | 1.641% | 0.6877% | 0.6877% | 0.6877% | 0.6877% | 1.283% | 1.283% | 1.283% | 1.283% | 0.6877% | 0.6877%
180 | 22 | 0.856% | 1.181% | 1.718% | 1.718% | 1.718% | 1.718% | 0.9246% | 0.9246% | 0.856% | 0.856% | 1.718% | 1.718%
180 | 23 | 3.159% | 0.6737% | 0.8111% | 0.6737% | 0.6737% | 0.6737% | 2.764% | 2.764% | 3.159% | 3.159% | 0.8111% | 0.6737%
180 | 24 | 2.352% | 0% | 0.3597% | 0% | 0% | 0% | 2.352% | 2.302% | 2.352% | 2.352% | 0.3597% | 0%
180 | 25 | 0.03029% | 0.5953% | 0.5953% | 0.5953% | 0.5953% | 0.5953% | 0.03029% | 0.08843% | 0.03029% | 0.03029% | 0.5953% | 0.5953%
180 | 26 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
180 | 27 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
180 | 28 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
180 | 29 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
180 | 30 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
180 | 31 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
180 | 32 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
180 | 33 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
180 | 34 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
180 | 35 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
180 | 36 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
180 | 37 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
180 | 38 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
180 | 39 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
180 | 40 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
210 | 0 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
210 | 1 | 21.74% | 5.942% | 5.942% | 5.942% | 5.942% | 5.942% | 21.74% | 21.74% | 21.74% | 21.74% | 5.942% | 5.942%
210 | 2 | 11.61% | 23.71% | 24.33% | 23.71% | 23.71% | 23.71% | 11.61% | 11.61% | 11.61% | 11.61% | 24.33% | 23.71%
210 | 3 | 13.2% | 11.56% | 11.6% | 11.51% | 11.56% | 11.51% | 13.2% | 13.3% | 13.2% | 13.2% | 11.6% | 11.56%
210 | 4 | 12.02% | 12.96% | 12.88% | 12.88% | 12.96% | 12.88% | 12.02% | 11.73% | 12.02% | 12.02% | 12.88% | 12.96%
210 | 5 | 11.04% | 12.63% | 12.63% | 12.63% | 12.63% | 12.63% | 11.04% | 11.04% | 11.04% | 11.04% | 12.63% | 12.63%
210 | 6 | 8.309% | 8.91% | 8.91% | 8.91% | 8.91% | 8.91% | 8.309% | 8.314% | 8.309% | 8.309% | 8.91% | 8.91%
210 | 7 | 6.308% | 6.441% | 6.462% | 6.441% | 6.441% | 6.441% | 6.308% | 6.301% | 6.308% | 6.308% | 6.462% | 6.441%
210 | 8 | 5.063% | 8.82% | 9.157% | 9.195% | 8.82% | 9.195% | 5.063% | 5.063% | 5.063% | 5.063% | 9.157% | 8.82%
210 | 9 | 4.962% | 7.701% | 7.383% | 7.383% | 7.701% | 7.383% | 4.959% | 4.959% | 4.962% | 4.962% | 7.383% | 7.701%
210 | 10 | 5.38% | 7.313% | 7.346% | 7.315% | 7.313% | 7.315% | 5.38% | 5.433% | 5.38% | 5.38% | 7.346% | 7.313%
210 | 11 | 3.806% | 4.508% | 4.525% | 4.543% | 4.517% | 4.543% | 3.806% | 4.032% | 3.806% | 3.806% | 4.525% | 4.517%
210 | 12 | 4.213% | 4.417% | 4.42% | 4.403% | 4.403% | 4.403% | 4.213% | 4.213% | 4.213% | 4.213% | 4.42% | 4.403%
210 | 13 | 4.483% | 3.758% | 3.757% | 3.769% | 3.758% | 3.769% | 4.483% | 4.483% | 4.483% | 4.483% | 3.757% | 3.758%
210 | 14 | 10.64% | 4.46% | 4.417% | 4.489% | 4.46% | 4.489% | 10.64% | 10.64% | 10.64% | 10.64% | 4.417% | 4.46%
210 | 15 | 9.781% | 5.18% | 5.284% | 5.284% | 5.448% | 5.284% | 9.781% | 9.781% | 9.781% | 9.781% | 5.284% | 5.448%
210 | 16 | 1.435% | 3.306% | 3.133% | 3.133% | 3.133% | 3.133% | 1.435% | 1.435% | 1.435% | 1.435% | 3.133% | 3.133%
210 | 17 | 14.71% | 6.211% | 7.186% | 6.016% | 6.016% | 6.016% | 14.71% | 15.51% | 14.71% | 14.71% | 7.186% | 6.016%
210 | 18 | 0.7748% | 3.962% | 1.765% | 3.962% | 3.962% | 3.962% | 0.7748% | 0.8684% | 0.7748% | 0.7748% | 1.765% | 3.962%
210 | 19 | 0% | 6.203% | 5.536% | 6.203% | 6.203% | 6.203% | 0% | 0% | 0% | 0% | 5.536% | 6.203%
210 | 20 | 1.826% | 1.573% | 1.573% | 1.573% | 1.573% | 1.573% | 1.826% | 1.826% | 1.826% | 1.826% | 1.573% | 1.573%
210 | 21 | 0.3335% | 0% | 0% | 0% | 0% | 0% | 0.3335% | 0.3335% | 0.3335% | 0.3335% | 0% | 0%
210 | 22 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
210 | 23 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
210 | 24 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
210 | 25 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
210 | 26 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
210 | 27 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
210 | 28 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
210 | 29 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
210 | 30 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
210 | 31 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
210 | 32 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
210 | 33 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
210 | 34 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
210 | 35 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
210 | 36 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
210 | 37 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
210 | 38 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
210 | 39 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
210 | 40 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
240 | 0 | 0% | 220.3% | 220.3% | 220.3% | 220.3% | 220.3% | 0% | 0% | 0% | 0% | 220.3% | 220.3%
240 | 1 | 10.4% | 29.88% | 29.88% | 29.88% | 29.88% | 29.88% | 10.4% | 10.4% | 10.4% | 10.4% | 29.88% | 29.88%
240 | 2 | 18.56% | 18.39% | 18.89% | 18.39% | 18.39% | 18.39% | 18.56% | 18.56% | 18.56% | 18.56% | 18.89% | 18.39%
240 | 3 | 12.86% | 16.64% | 16.31% | 16.64% | 16.64% | 16.64% | 12.86% | 12.2% | 12.86% | 12.86% | 16.31% | 16.64%
240 | 4 | 11.41% | 11.51% | 11.51% | 11.51% | 11.51% | 11.51% | 11.41% | 12.39% | 11.41% | 11.41% | 11.51% | 11.51%
240 | 5 | 11.06% | 11.25% | 11.25% | 11.25% | 11.25% | 11.25% | 11.06% | 11.06% | 11.06% | 11.06% | 11.25% | 11.25%
240 | 6 | 8.119% | 9.148% | 8.819% | 8.819% | 8.819% | 8.819% | 8.119% | 8.119% | 8.119% | 8.119% | 8.819% | 8.819%
240 | 7 | 7.423% | 8.079% | 8.405% | 8.405% | 8.405% | 8.405% | 7.423% | 7.423% | 7.423% | 7.423% | 8.405% | 8.405%
240 | 8 | 6.329% | 9.016% | 9.273% | 9.241% | 9.016% | 9.241% | 6.329% | 6.329% | 6.329% | 6.329% | 9.273% | 9.016%
240 | 9 | 10.04% | 6.167% | 6.019% | 6.044% | 6.167% | 6.044% | 10.04% | 10.04% | 10.04% | 10.04% | 6.019% | 6.167%
240 | 10 | 5.851% | 4.851% | 4.843% | 4.851% | 4.851% | 4.851% | 5.851% | 5.923% | 5.851% | 5.851% | 4.843% | 4.851%
240 | 11 | 4.438% | 4.761% | 4.772% | 4.761% | 4.761% | 4.761% | 4.438% | 4.543% | 4.438% | 4.438% | 4.772% | 4.761%
240 | 12 | 4.474% | 3.678% | 3.678% | 3.678% | 3.678% | 3.678% | 4.474% | 4.474% | 4.474% | 4.474% | 3.678% | 3.678%
240 | 13 | 5.241% | 4.443% | 4.528% | 4.443% | 4.443% | 4.443% | 5.241% | 5.235% | 5.241% | 5.241% | 4.528% | 4.443%
240 | 14 | 5.166% | 3.986% | 3.907% | 3.986% | 3.986% | 3.986% | 5.166% | 5.204% | 5.166% | 5.166% | 3.907% | 3.986%
240 | 15 | 3.666% | 2.623% | 2.678% | 2.678% | 2.678% | 2.678% | 3.852% | 3.852% | 3.666% | 3.666% | 2.678% | 2.678%
240 | 16 | 3.603% | 2.118% | 2.013% | 2.013% | 2.013% | 2.013% | 3.608% | 3.608% | 3.603% | 3.603% | 2.013% | 2.013%
240 | 17 | 8.343% | 3.047% | 3.047% | 3.047% | 3.047% | 3.047% | 8.343% | 8.343% | 8.343% | 8.343% | 3.047% | 3.047%
240 | 18 | 0% | 2.214% | 2.214% | 2.214% | 2.214% | 2.214% | 0% | 0% | 0% | 0% | 2.214% | 2.214%
240 | 19 | 2.426% | 2.097% | 2.097% | 2.097% | 2.097% | 2.097% | 2.426% | 2.736% | 2.426% | 2.426% | 2.097% | 2.097%
240 | 20 | 3.707% | 1.508% | 1.508% | 1.508% | 1.508% | 1.508% | 3.707% | 3.277% | 3.707% | 3.707% | 1.508% | 1.508%
240 | 21 | 0% | 1.427% | 0.5037% | 0.5037% | 0.5037% | 0.5037% | 0% | 0% | 0% | 0% | 0.5037% | 0.5037%
240 | 22 | 1.112% | 0% | 1.912% | 1.912% | 1.912% | 1.912% | 1.112% | 1.112% | 1.112% | 1.112% | 1.912% | 1.912%
240 | 23 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
240 | 24 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
240 | 25 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
240 | 26 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
240 | 27 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
240 | 28 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
240 | 29 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
240 | 30 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
240 | 31 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
240 | 32 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
240 | 33 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
240 | 34 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
240 | 35 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
240 | 36 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
240 | 37 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
240 | 38 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
240 | 39 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
240 | 40 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
270 | 0 | 40.99% | 0% | 0% | 0% | 0% | 0% | 40.99% | 40.99% | 40.99% | 40.99% | 0% | 0%
270 | 1 | 10.91% | 14.26% | 14.26% | 14.26% | 14.26% | 14.26% | 10.91% | 10.91% | 10.91% | 10.91% | 14.26% | 14.26%
270 | 2 | 13.83% | 15.15% | 15.83% | 15.27% | 15.27% | 15.27% | 13.83% | 13.83% | 13.83% | 13.83% | 15.83% | 15.27%
270 | 3 | 16.24% | 14.06% | 13.87% | 14.13% | 14.13% | 14.13% | 16.24% | 16.43% | 16.24% | 16.24% | 13.87% | 14.13%
270 | 4 | 9.579% | 9.296% | 9.296% | 9.296% | 9.296% | 9.296% | 9.579% | 9.56% | 9.579% | 9.579% | 9.296% | 9.296%
270 | 5 | 7.998% | 9.086% | 9.086% | 9.086% | 9.086% | 9.086% | 7.998% | 7.998% | 7.998% | 7.998% | 9.086% | 9.086%
270 | 6 | 9.01% | 7.796% | 7.803% | 7.785% | 7.785% | 7.785% | 9.01% | 9.026% | 9.01% | 9.01% | 7.803% | 7.785%
270 | 7 | 8.725% | 6.676% | 6.706% | 6.694% | 6.681% | 6.694% | 8.725% | 8.703% | 8.725% | 8.725% | 6.706% | 6.681%
270 | 8 | 5.952% | 5.492% | 5.61% | 5.622% | 5.5% | 5.622% | 5.961% | 5.961% | 5.952% | 5.952% | 5.61% | 5.5%
270 | 9 | 8.671% | 5.274% | 5.172% | 5.157% | 5.27% | 5.157% | 8.646% | 8.646% | 8.671% | 8.671% | 5.172% | 5.27%
270 | 10 | 5.252% | 4.199% | 4.216% | 4.227% | 4.199% | 4.227% | 5.252% | 5.376% | 5.252% | 5.252% | 4.216% | 4.199%
270 | 11 | 5.295% | 4.857% | 4.862% | 4.848% | 4.87% | 4.848% | 5.295% | 5.175% | 5.295% | 5.295% | 4.862% | 4.87%
270 | 12 | 5.462% | 5.777% | 5.723% | 5.751% | 5.751% | 5.751% | 5.462% | 5.462% | 5.462% | 5.462% | 5.723% | 5.751%
270 | 13 | 5.878% | 5.125% | 5.194% | 5.125% | 5.125% | 5.125% | 5.878% | 5.491% | 5.878% | 5.878% | 5.194% | 5.125%
270 | 14 | 6.292% | 4.304% | 4.102% | 4.163% | 4.304% | 4.163% | 6.292% | 6.68% | 6.292% | 6.292% | 4.102% | 4.304%
270 | 15 | 3.897% | 3.085% | 3.61% | 3.61% | 3.03% | 3.61% | 3.875% | 3.829% | 3.897% | 3.897% | 3.61% | 3.03%
270 | 16 | 4.125% | 3.706% | 3.586% | 3.586% | 3.586% | 3.586% | 4.114% | 4.12% | 4.125% | 4.125% | 3.586% | 3.586%
270 | 17 | 5.517% | 4.402% | 4.61% | 4.402% | 4.402% | 4.402% | 5.517% | 5.556% | 5.517% | 5.517% | 4.61% | 4.402%
270 | 18 | 6.295% | 2.655% | 2.532% | 2.655% | 2.655% | 2.655% | 6.295% | 5.395% | 6.295% | 6.295% | 2.532% | 2.655%
270 | 19 | 2.957% | 3.436% | 3.436% | 3.436% | 3.436% | 3.436% | 2.957% | 2.957% | 2.957% | 2.957% | 3.436% | 3.436%
270 | 20 | 0% | 2.658% | 2.627% | 2.627% | 2.658% | 2.627% | 0% | 0% | 0% | 0% | 2.627% | 2.658%
270 | 21 | 2.357% | 1.516% | 1.779% | 1.779% | 1.516% | 1.779% | 2.357% | 2.357% | 2.357% | 2.357% | 1.779% | 1.516%
270 | 22 | 0% | 1.44% | 1.44% | 1.44% | 1.44% | 1.44% | 0% | 0% | 0% | 0% | 1.44% | 1.44%
270 | 23 | 0.3338% | 0% | 0% | 0% | 0% | 0% | 0.3338% | 0.3338% | 0.3338% | 0.3338% | 0% | 0%
270 | 24 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
270 | 25 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
270 | 26 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
270 | 27 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
270 | 28 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
270 | 29 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
270 | 30 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
270 | 31 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
270 | 32 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
270 | 33 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
270 | 34 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
270 | 35 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
270 | 36 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
270 | 37 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
270 | 38 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
270 | 39 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
270 | 40 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
300 | 0 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
300 | 1 | 18.18% | 23.16% | 23.16% | 23.16% | 23.16% | 23.16% | 18.18% | 18.18% | 18.18% | 18.18% | 23.16% | 23.16%
300 | 2 | 16.51% | 13.71% | 13.46% | 13.71% | 13.71% | 13.71% | 16.51% | 16.24% | 16.51% | 16.51% | 13.46% | 13.71%
300 | 3 | 13.3% | 17.14% | 16.7% | 17.14% | 17.14% | 17.14% | 13.3% | 13.9% | 13.3% | 13.3% | 16.7% | 17.14%
300 | 4 | 11.88% | 11.3% | 11.32% | 11.3% | 11.3% | 11.3% | 11.9% | 11.98% | 11.88% | 11.88% | 11.32% | 11.3%
300 | 5 | 9.628% | 8.451% | 8.429% | 8.451% | 8.451% | 8.451% | 9.67% | 9.679% | 9.628% | 9.628% | 8.429% | 8.451%
300 | 6 | 7.876% | 7.915% | 7.9% | 7.9% | 7.9% | 7.9% | 7.876% | 7.797% | 7.876% | 7.876% | 7.9% | 7.9%
300 | 7 | 6.34% | 6.278% | 6.333% | 6.333% | 6.333% | 6.333% | 6.34% | 6.521% | 6.34% | 6.34% | 6.333% | 6.333%
300 | 8 | 5.731% | 5.291% | 5.39% | 5.39% | 5.292% | 5.39% | 5.745% | 5.745% | 5.731% | 5.731% | 5.39% | 5.292%
300 | 9 | 5.548% | 6.048% | 5.881% | 5.87% | 6.047% | 5.87% | 5.54% | 5.54% | 5.548% | 5.548% | 5.881% | 6.047%
300 | 10 | 6.598% | 5.479% | 5.138% | 5.134% | 5.479% | 5.134% | 6.598% | 6.111% | 6.598% | 6.598% | 5.138% | 5.479%
300 | 11 | 7.268% | 4.382% | 4.901% | 4.926% | 4.382% | 4.926% | 7.268% | 7.582% | 7.268% | 7.268% | 4.901% | 4.382%
300 | 12 | 5.578% | 3.98% | 3.965% | 3.98% | 3.98% | 3.98% | 5.578% | 5.578% | 5.578% | 5.578% | 3.965% | 3.98%
300 | 13 | 4.365% | 4.125% | 4.148% | 4.125% | 4.125% | 4.125% | 4.365% | 4.365% | 4.365% | 4.365% | 4.148% | 4.125%
300 | 14 | 4.204% | 6.638% | 5.481% | 5.507% | 6.638% | 5.507% | 4.204% | 4.204% | 4.204% | 4.204% | 5.481% | 6.638%
300 | 15 | 5.494% | 5.905% | 6.847% | 6.847% | 5.05% | 6.847% | 5.522% | 5.522% | 5.494% | 5.494% | 6.847% | 5.05%
300 | 16 | 10.12% | 6.9% | 7.507% | 7.326% | 7.326% | 7.326% | 10.03% | 10.03% | 10.12% | 10.12% | 7.507% | 7.326%
300 | 17 | 9.37% | 4.474% | 1.648% | 4.474% | 4.474% | 4.474% | 9.37% | 10.22% | 9.37% | 9.37% | 1.648% | 4.474%
300 | 18 | 3.404% | 8.666% | 8.763% | 8.666% | 8.666% | 8.666% | 3.404% | 3.287% | 3.404% | 3.404% | 8.763% | 8.666%
300 | 19 | 0.2649% | 1.84% | 1.84% | 1.84% | 1.84% | 1.84% | 0.2649% | 0.2649% | 0.2649% | 0.2649% | 1.84% | 1.84%
300 | 20 | 3.67% | 0% | 0% | 0% | 0% | 0% | 3.67% | 3.67% | 3.67% | 3.67% | 0% | 0%
300 | 21 | 0% | 0.3889% | 0.3889% | 0.3889% | 0.3889% | 0.3889% | 0% | 0% | 0% | 0% | 0.3889% | 0.3889%
300 | 22 | 1.474% | 0.5463% | 0.5463% | 0.5463% | 0.5463% | 0.5463% | 1.702% | 1.702% | 1.474% | 1.474% | 0.5463% | 0.5463%
300 | 23 | 0% | 0% | 0% | 0% | 0% | 0% | 0.8481% | 0.8481% | 0% | 0% | 0% | 0%
300 | 24 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
300 | 25 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
300 | 26 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
300 | 27 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
300 | 28 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
300 | 29 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
300 | 30 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
300 | 31 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
300 | 32 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
300 | 33 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
300 | 34 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
300 | 35 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
300 | 36 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
300 | 37 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
300 | 38 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
300 | 39 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
300 | 40 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
330 | 0 | 35.36% | 0% | 0% | 0% | 0% | 0% | 35.36% | 35.36% | 35.36% | 35.36% | 0% | 0%
330 | 1 | 8.777% | 39.76% | 39.76% | 39.76% | 39.76% | 39.76% | 8.777% | 8.777% | 8.777% | 8.777% | 39.76% | 39.76%
330 | 2 | 18.63% | 22.3% | 23.2% | 22.3% | 22.3% | 22.3% | 18.63% | 18.63% | 18.63% | 18.63% | 23.2% | 22.3%
330 | 3 | 13.83% | 12.22% | 12.55% | 12.22% | 12.22% | 12.22% | 13.83% | 13.84% | 13.83% | 13.83% | 12.55% | 12.22%
330 | 4 | 12.29% | 10.98% | 10.98% | 10.98% | 10.98% | 10.98% | 12.34% | 12.37% | 12.29% | 12.29% | 10.98% | 10.98%
330 | 5 | 10.81% | 9.741% | 9.741% | 9.741% | 9.741% | 9.741% | 10.82% | 10.82% | 10.81% | 10.81% | 9.741% | 9.741%
330 | 6 | 7.271% | 7.687% | 7.708% | 7.704% | 7.704% | 7.704% | 7.353% | 7.353% | 7.271% | 7.271% | 7.708% | 7.704%
330 | 7 | 6.12% | 8.076% | 8.086% | 8.098% | 8.077% | 8.098% | 6.12% | 6.12% | 6.12% | 6.12% | 8.086% | 8.077%
330 | 8 | 7.448% | 5.269% | 5.29% | 5.29% | 5.259% | 5.29% | 7.471% | 7.471% | 7.448% | 7.448% | 5.29% | 5.259%
330 | 9 | 5.371% | 5.859% | 5.769% | 5.758% | 5.859% | 5.758% | 5.359% | 5.359% | 5.371% | 5.371% | 5.769% | 5.859%
330 | 10 | 4.468% | 5.65% | 5.651% | 5.671% | 5.65% | 5.671% | 4.468% | 4.593% | 4.468% | 4.468% | 5.651% | 5.65%
330 | 11 | 4.577% | 4.43% | 4.456% | 4.431% | 4.452% | 4.431% | 4.577% | 4.429% | 4.577% | 4.577% | 4.456% | 4.452%
330 | 12 | 4.144% | 4.049% | 4.018% | 4.018% | 4.018% | 4.018% | 4.144% | 4.163% | 4.144% | 4.144% | 4.018% | 4.018%
330 | 13 | 3.512% | 4.645% | 4.689% | 4.643% | 4.643% | 4.643% | 3.512% | 3.485% | 3.512% | 3.512% | 4.689% | 4.643%
330 | 14 | 7.085% | 4.975% | 4.971% | 5.139% | 4.975% | 5.139% | 7.085% | 7.085% | 7.085% | 7.085% | 4.971% | 4.975%
330 | 15 | 3.383% | 3.041% | 2.732% | 2.86% | 3.036% | 2.86% | 3.045% | 3.045% | 3.383% | 3.383% | 2.732% | 3.036%
330 | 16 | 2.558% | 4.47% | 4.426% | 4.523% | 4.523% | 4.523% | 3.125% | 3.125% | 2.558% | 2.558% | 4.426% | 4.523%
330 | 17 | 3.025% | 5.392% | 5.392% | 5.392% | 5.392% | 5.392% | 3.025% | 3.216% | 3.025% | 3.025% | 5.392% | 5.392%
330 | 18 | 0.8919% | 6.555% | 1.73% | 6.555% | 6.555% | 6.555% | 0.8919% | 0.6492% | 0.8919% | 0.8919% | 1.73% | 6.555%
330 | 19 | 2.142% | 1.647% | 7.258% | 1.773% | 1.647% | 1.773% | 2.142% | 2.142% | 2.142% | 2.142% | 7.258% | 1.647%
330 | 20 | 1.978% | 1.433% | 1.392% | 1.392% | 1.433% | 1.392% | 1.978% | 1.978% | 1.978% | 1.978% | 1.392% | 1.433%
330 | 21 | 5.392% | 1.916% | 1.916% | 1.916% | 1.916% | 1.916% | 5.392% | 5.392% | 5.392% | 5.392% | 1.916% | 1.916%
330 | 22 | 2.142% | 0.4546% | 0.4546% | 0.4546% | 0.4546% | 0.4546% | 0.7438% | 0.7438% | 2.142% | 2.142% | 0.4546% | 0.4546%
330 | 23 | 0% | 0% | 0% | 0% | 0% | 0% | 1.897% | 1.897% | 0% | 0% | 0% | 0%
330 | 24 | 0.1645% | 0% | 0% | 0% | 0% | 0% | 0.1645% | 0.1876% | 0.1645% | 0.1645% | 0% | 0%
330 | 25 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.101% | 0% | 0% | 0% | 0%
330 | 26 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
330 | 27 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
330 | 28 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
330 | 29 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
330 | 30 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
330 | 31 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
330 | 32 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
330 | 33 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
330 | 34 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
330 | 35 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
330 | 36 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
330 | 37 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
330 | 38 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
330 | 39 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
330 | 40 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108

## Extreme Ambient TI
Extreme Ambient Turbulence Intensity (10-minute WS SD/10-minute mean WS) [%] {I(wind speed, direction)}
|  | Measurement Device |  | Wind Turbine
Wind Direction (Midpoint) (°) | Wind Speed (Midpoint) (m/s) | Gobblers Knob West | Gobblers Knob East | 97 | 98 | 100 | 102 | 103 | 104 | 105 | 106 | 107 | 108
ALL | 0 | 193.3% | 361.5% | 361.5% | 361.5% | 361.5% | 361.5% | 193.3% | 193.3% | 193.3% | 193.3% | 361.5% | 361.5%
ALL | 1 | 183.1% | 294.8% | 294.8% | 294.8% | 294.8% | 294.8% | 183.1% | 183.1% | 183.1% | 183.1% | 294.8% | 294.8%
ALL | 2 | 112.2% | 167.5% | 167.5% | 167.5% | 167.5% | 167.5% | 112.2% | 112.2% | 112.2% | 112.2% | 167.5% | 167.5%
ALL | 3 | 96.2% | 115.6% | 115.6% | 115.6% | 115.6% | 115.6% | 96.2% | 96.2% | 96.2% | 96.2% | 115.6% | 115.6%
ALL | 4 | 85.14% | 93.72% | 93.72% | 93.72% | 93.72% | 93.72% | 85.14% | 85.14% | 85.14% | 85.14% | 93.72% | 93.72%
ALL | 5 | 82.24% | 80.98% | 80.98% | 80.98% | 80.98% | 80.98% | 82.24% | 82.24% | 82.24% | 82.24% | 80.98% | 80.98%
ALL | 6 | 97.95% | 74.54% | 74.54% | 74.54% | 74.54% | 74.54% | 97.95% | 97.95% | 97.95% | 97.95% | 74.54% | 74.54%
ALL | 7 | 64.27% | 74.13% | 74.13% | 74.13% | 74.13% | 74.13% | 64.27% | 64.27% | 64.27% | 64.27% | 74.13% | 74.13%
ALL | 8 | 69.14% | 79.17% | 79.17% | 79.17% | 79.17% | 79.17% | 69.14% | 69.14% | 69.14% | 69.14% | 79.17% | 79.17%
ALL | 9 | 92.37% | 51.94% | 51.94% | 51.94% | 51.94% | 51.94% | 92.37% | 92.37% | 92.37% | 92.37% | 51.94% | 51.94%
ALL | 10 | 54.46% | 68.64% | 68.64% | 68.64% | 68.64% | 68.64% | 54.1% | 54.1% | 54.1% | 54.1% | 68.64% | 68.64%
ALL | 11 | 74.49% | 53.18% | 53.18% | 53.18% | 53.18% | 53.18% | 74.49% | 54.46% | 74.49% | 74.49% | 53.18% | 53.18%
ALL | 12 | 39.4% | 51.45% | 51.45% | 51.45% | 51.45% | 51.45% | 39.4% | 74.49% | 39.4% | 39.4% | 51.45% | 51.45%
ALL | 13 | 44.25% | 43.48% | 43.48% | 43.48% | 43.48% | 43.48% | 44.25% | 44.25% | 44.25% | 44.25% | 43.48% | 43.48%
ALL | 14 | 68.63% | 41.61% | 41.61% | 41.61% | 41.61% | 41.61% | 68.63% | 68.63% | 68.63% | 68.63% | 41.61% | 41.61%
ALL | 15 | 52.28% | 39.43% | 37.5% | 37.5% | 35.64% | 37.5% | 52.28% | 33.07% | 52.28% | 52.28% | 37.5% | 35.64%
ALL | 16 | 48.96% | 36.23% | 39.43% | 39.43% | 39.43% | 39.43% | 22.22% | 52.28% | 22.22% | 22.22% | 39.43% | 39.43%
ALL | 17 | 46.64% | 34.45% | 34.45% | 34.45% | 34.45% | 34.45% | 48.96% | 48.96% | 48.96% | 48.96% | 34.45% | 34.45%
ALL | 18 | 18.17% | 35.63% | 35.63% | 35.63% | 35.63% | 35.63% | 18.17% | 36.25% | 18.17% | 18.17% | 35.63% | 35.63%
ALL | 19 | 19.4% | 18.78% | 30.68% | 18.78% | 18.78% | 18.78% | 19.4% | 19.4% | 19.4% | 19.4% | 30.68% | 18.78%
ALL | 20 | 19.64% | 17.8% | 17.8% | 17.8% | 17.8% | 17.8% | 19.64% | 19.64% | 19.64% | 19.64% | 17.8% | 17.8%
ALL | 21 | 25.55% | 15.38% | 15.38% | 15.38% | 15.38% | 15.38% | 25.55% | 25.55% | 25.55% | 25.55% | 15.38% | 15.38%
ALL | 22 | 13.87% | 31.96% | 31.96% | 31.96% | 31.96% | 31.96% | 15.77% | 15.77% | 15.77% | 15.77% | 31.96% | 31.96%
ALL | 23 | 17.01% | 15.34% | 15.34% | 15.34% | 15.34% | 15.34% | 17.01% | 17.01% | 17.01% | 17.01% | 15.34% | 15.34%
ALL | 24 | 21.47% | 7.684% | 7.721% | 7.684% | 7.684% | 7.684% | 21.47% | 21.47% | 21.47% | 21.47% | 7.721% | 7.684%
ALL | 25 | 8.929% | 8.644% | 8.644% | 8.644% | 8.644% | 8.644% | 9.056% | 9.056% | 9.056% | 9.056% | 8.644% | 8.644%
ALL | 26 | 22.36% | 9.739% | 9.739% | 9.739% | 9.739% | 9.739% | 22.36% | 22.36% | 22.36% | 22.36% | 9.739% | 9.739%
ALL | 27 | 9.924% | 9.743% | 9.743% | 9.743% | 9.743% | 9.743% | 9.924% | 9.924% | 9.924% | 9.924% | 9.743% | 9.743%
ALL | 28 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
ALL | 29 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
ALL | 30 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
ALL | 31 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
ALL | 32 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
ALL | 33 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
ALL | 34 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
ALL | 35 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
ALL | 36 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
ALL | 37 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
ALL | 38 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
ALL | 39 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108
ALL | 40 | 0% | 0% | bar: Wind Turbine 97 to Wind Turbine 108

## Temperature
Yearly mean ambient Temperature [θmean] (°C)
| Measurement Device |  |  |  | Wind Turbine
| Gobblers Knob West | Number of samples | Gobblers Knob East | Number of samples | 97 | Number of samples | 98 | Number of samples | 100 | Number of samples | 102 | Number of samples | 103 | Number of samples | 104 | Number of samples | 105 | Number of samples | 106 | Number of samples | 107 | Number of samples | 108 | Number of samples
Yearly mean ambient Temperature [θmean] | 11.5 |  | 11.4 |  | 11.4 |  | 11.4 |  | 11.4 |  | 11.4 |  | 11.4 |  | 11.4 |  | 11.4 |  | 11.4 |  | 11.4 |  | 11.4
Days per year with at least 1 hour below -20 deg °C | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
Temperature (C) | Temperature Frequency Distribution (% and number of samples)
<=-40 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0
-39 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0
-38 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0
-37 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0
-36 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0
-35 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0
-34 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0
-33 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0
-32 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0
-31 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0
-30 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0
-29 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0
-28 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0
-27 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0
-26 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0
-25 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0
-24 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0
-23 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0
-22 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0
-21 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0
-20 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0
-19 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0
-18 | 0.07991% | 7 | 0.1256% | 11 | 0.1256% | 11 | 0.1256% | 11 | 0.1256% | 11 | 0.1256% | 11 | 0.1256% | 11 | 0.1256% | 11 | 0.1256% | 11 | 0.1256% | 11 | 0.1256% | 11 | 0.1256% | 11
-17 | 0.2397% | 21 | 0.1712% | 15 | 0.1712% | 15 | 0.1712% | 15 | 0.1712% | 15 | 0.1712% | 15 | 0.1712% | 15 | 0.1712% | 15 | 0.1712% | 15 | 0.1712% | 15 | 0.1712% | 15 | 0.1712% | 15
-16 | 0.05708% | 5 | 0.05708% | 5 | 0.05708% | 5 | 0.05708% | 5 | 0.05708% | 5 | 0.05708% | 5 | 0.05708% | 5 | 0.05708% | 5 | 0.05708% | 5 | 0.05708% | 5 | 0.05708% | 5 | 0.05708% | 5
-15 | 0.09132% | 8 | 0.09132% | 8 | 0.09132% | 8 | 0.09132% | 8 | 0.09132% | 8 | 0.09132% | 8 | 0.09132% | 8 | 0.09132% | 8 | 0.09132% | 8 | 0.09132% | 8 | 0.09132% | 8 | 0.09132% | 8
-14 | 0.137% | 12 | 0.1826% | 16 | 0.1826% | 16 | 0.1826% | 16 | 0.1826% | 16 | 0.1826% | 16 | 0.1826% | 16 | 0.1826% | 16 | 0.1826% | 16 | 0.1826% | 16 | 0.1826% | 16 | 0.1826% | 16
-13 | 0.07991% | 7 | 0.09132% | 8 | 0.09132% | 8 | 0.09132% | 8 | 0.09132% | 8 | 0.09132% | 8 | 0.09132% | 8 | 0.09132% | 8 | 0.09132% | 8 | 0.09132% | 8 | 0.09132% | 8 | 0.09132% | 8
-12 | 0.2968% | 26 | 0.3881% | 34 | 0.3881% | 34 | 0.3881% | 34 | 0.3881% | 34 | 0.3881% | 34 | 0.3881% | 34 | 0.3881% | 34 | 0.3881% | 34 | 0.3881% | 34 | 0.3881% | 34 | 0.3881% | 34
-11 | 0.274% | 24 | 0.2854% | 25 | 0.2854% | 25 | 0.2854% | 25 | 0.2854% | 25 | 0.2854% | 25 | 0.2854% | 25 | 0.2854% | 25 | 0.2854% | 25 | 0.2854% | 25 | 0.2854% | 25 | 0.2854% | 25
-10 | 0.5936% | 52 | 0.4795% | 42 | 0.4795% | 42 | 0.4795% | 42 | 0.4795% | 42 | 0.4795% | 42 | 0.4795% | 42 | 0.4795% | 42 | 0.4795% | 42 | 0.4795% | 42 | 0.4795% | 42 | 0.4795% | 42
-9 | 0.7763% | 68 | 0.5708% | 50 | 0.5708% | 50 | 0.5708% | 50 | 0.5708% | 50 | 0.5708% | 50 | 0.5708% | 50 | 0.5708% | 50 | 0.5708% | 50 | 0.5708% | 50 | 0.5708% | 50 | 0.5708% | 50
-8 | 0.7534% | 66 | 0.6849% | 60 | 0.6849% | 60 | 0.6849% | 60 | 0.6849% | 60 | 0.6849% | 60 | 0.6849% | 60 | 0.6849% | 60 | 0.6849% | 60 | 0.6849% | 60 | 0.6849% | 60 | 0.6849% | 60
-7 | 0.7534% | 66 | 0.9589% | 84 | 0.9589% | 84 | 0.9589% | 84 | 0.9589% | 84 | 0.9589% | 84 | 0.9589% | 84 | 0.9589% | 84 | 0.9589% | 84 | 0.9589% | 84 | 0.9589% | 84 | 0.9589% | 84
-6 | 1.29% | 113 | 1.221% | 107 | 1.221% | 107 | 1.221% | 107 | 1.221% | 107 | 1.221% | 107 | 1.221% | 107 | 1.221% | 107 | 1.221% | 107 | 1.221% | 107 | 1.221% | 107 | 1.221% | 107
-5 | 1.758% | 154 | 1.952% | 171 | 1.952% | 171 | 1.952% | 171 | 1.952% | 171 | 1.952% | 171 | 1.952% | 171 | 1.952% | 171 | 1.952% | 171 | 1.952% | 171 | 1.952% | 171 | 1.952% | 171
-4 | 1.758% | 154 | 1.872% | 164 | 1.872% | 164 | 1.872% | 164 | 1.872% | 164 | 1.872% | 164 | 1.872% | 164 | 1.872% | 164 | 1.872% | 164 | 1.872% | 164 | 1.872% | 164 | 1.872% | 164
-3 | 1.906% | 167 | 2.009% | 176 | 2.009% | 176 | 2.009% | 176 | 2.009% | 176 | 2.009% | 176 | 2.009% | 176 | 2.009% | 176 | 2.009% | 176 | 2.009% | 176 | 2.009% | 176 | 2.009% | 176
-2 | 2.694% | 236 | 2.717% | 238 | 2.717% | 238 | 2.717% | 238 | 2.717% | 238 | 2.717% | 238 | 2.717% | 238 | 2.717% | 238 | 2.717% | 238 | 2.717% | 238 | 2.717% | 238 | 2.717% | 238
-1 | 2.568% | 225 | 2.489% | 218 | 2.489% | 218 | 2.489% | 218 | 2.489% | 218 | 2.489% | 218 | 2.489% | 218 | 2.489% | 218 | 2.489% | 218 | 2.489% | 218 | 2.489% | 218 | 2.489% | 218
0 | 2.511% | 220 | 2.466% | 216 | 2.466% | 216 | 2.466% | 216 | 2.466% | 216 | 2.466% | 216 | 2.466% | 216 | 2.466% | 216 | 2.466% | 216 | 2.466% | 216 | 2.466% | 216 | 2.466% | 216
1 | 2.534% | 222 | 2.797% | 245 | 2.797% | 245 | 2.797% | 245 | 2.797% | 245 | 2.797% | 245 | 2.797% | 245 | 2.797% | 245 | 2.797% | 245 | 2.797% | 245 | 2.797% | 245 | 2.797% | 245
2 | 2.911% | 255 | 2.557% | 224 | 2.557% | 224 | 2.557% | 224 | 2.557% | 224 | 2.557% | 224 | 2.557% | 224 | 2.557% | 224 | 2.557% | 224 | 2.557% | 224 | 2.557% | 224 | 2.557% | 224
3 | 3.881% | 340 | 3.653% | 320 | 3.653% | 320 | 3.653% | 320 | 3.653% | 320 | 3.653% | 320 | 3.653% | 320 | 3.653% | 320 | 3.653% | 320 | 3.653% | 320 | 3.653% | 320 | 3.653% | 320
4 | 2.808% | 246 | 2.728% | 239 | 2.728% | 239 | 2.728% | 239 | 2.728% | 239 | 2.728% | 239 | 2.728% | 239 | 2.728% | 239 | 2.728% | 239 | 2.728% | 239 | 2.728% | 239 | 2.728% | 239
5 | 2.763% | 242 | 2.808% | 246 | 2.808% | 246 | 2.808% | 246 | 2.808% | 246 | 2.808% | 246 | 2.808% | 246 | 2.808% | 246 | 2.808% | 246 | 2.808% | 246 | 2.808% | 246 | 2.808% | 246
6 | 2.717% | 238 | 2.763% | 242 | 2.763% | 242 | 2.763% | 242 | 2.763% | 242 | 2.763% | 242 | 2.763% | 242 | 2.763% | 242 | 2.763% | 242 | 2.763% | 242 | 2.763% | 242 | 2.763% | 242
7 | 3.322% | 291 | 3.333% | 292 | 3.333% | 292 | 3.333% | 292 | 3.333% | 292 | 3.333% | 292 | 3.333% | 292 | 3.333% | 292 | 3.333% | 292 | 3.333% | 292 | 3.333% | 292 | 3.333% | 292
8 | 2.363% | 207 | 2.568% | 225 | 2.568% | 225 | 2.568% | 225 | 2.568% | 225 | 2.568% | 225 | 2.568% | 225 | 2.568% | 225 | 2.568% | 225 | 2.568% | 225 | 2.568% | 225 | 2.568% | 225
9 | 2.329% | 204 | 2.192% | 192 | 2.192% | 192 | 2.192% | 192 | 2.192% | 192 | 2.192% | 192 | 2.192% | 192 | 2.192% | 192 | 2.192% | 192 | 2.192% | 192 | 2.192% | 192 | 2.192% | 192
10 | 2.877% | 252 | 3.037% | 266 | 3.037% | 266 | 3.037% | 266 | 3.037% | 266 | 3.037% | 266 | 3.037% | 266 | 3.037% | 266 | 3.037% | 266 | 3.037% | 266 | 3.037% | 266 | 3.037% | 266
11 | 1.564% | 137 | 1.45% | 127 | 1.45% | 127 | 1.45% | 127 | 1.45% | 127 | 1.45% | 127 | 1.45% | 127 | 1.45% | 127 | 1.45% | 127 | 1.45% | 127 | 1.45% | 127 | 1.45% | 127
12 | 2.477% | 217 | 2.968% | 260 | 2.968% | 260 | 2.968% | 260 | 2.968% | 260 | 2.968% | 260 | 2.968% | 260 | 2.968% | 260 | 2.968% | 260 | 2.968% | 260 | 2.968% | 260 | 2.968% | 260
13 | 2.226% | 195 | 2.306% | 202 | 2.306% | 202 | 2.306% | 202 | 2.306% | 202 | 2.306% | 202 | 2.306% | 202 | 2.306% | 202 | 2.306% | 202 | 2.306% | 202 | 2.306% | 202 | 2.306% | 202
14 | 3.527% | 309 | 3.676% | 322 | 3.676% | 322 | 3.676% | 322 | 3.676% | 322 | 3.676% | 322 | 3.676% | 322 | 3.676% | 322 | 3.676% | 322 | 3.676% | 322 | 3.676% | 322 | 3.676% | 322
15 | 1.872% | 164 | 1.963% | 172 | 1.963% | 172 | 1.963% | 172 | 1.963% | 172 | 1.963% | 172 | 1.963% | 172 | 1.963% | 172 | 1.963% | 172 | 1.963% | 172 | 1.963% | 172 | 1.963% | 172
16 | 3.961% | 347 | 3.995% | 350 | 3.995% | 350 | 3.995% | 350 | 3.995% | 350 | 3.995% | 350 | 3.995% | 350 | 3.995% | 350 | 3.995% | 350 | 3.995% | 350 | 3.995% | 350 | 3.995% | 350
17 | 3.539% | 310 | 3.527% | 309 | 3.527% | 309 | 3.527% | 309 | 3.527% | 309 | 3.527% | 309 | 3.527% | 309 | 3.527% | 309 | 3.527% | 309 | 3.527% | 309 | 3.527% | 309 | 3.527% | 309
18 | 3.55% | 311 | 3.584% | 314 | 3.584% | 314 | 3.584% | 314 | 3.584% | 314 | 3.584% | 314 | 3.584% | 314 | 3.584% | 314 | 3.584% | 314 | 3.584% | 314 | 3.584% | 314 | 3.584% | 314
19 | 4.384% | 384 | 4.384% | 384 | 4.384% | 384 | 4.384% | 384 | 4.384% | 384 | 4.384% | 384 | 4.384% | 384 | 4.384% | 384 | 4.384% | 384 | 4.384% | 384 | 4.384% | 384 | 4.384% | 384
20 | 2.957% | 259 | 2.9% | 254 | 2.9% | 254 | 2.9% | 254 | 2.9% | 254 | 2.9% | 254 | 2.9% | 254 | 2.9% | 254 | 2.9% | 254 | 2.9% | 254 | 2.9% | 254 | 2.9% | 254
21 | 2.603% | 228 | 2.546% | 223 | 2.546% | 223 | 2.546% | 223 | 2.546% | 223 | 2.546% | 223 | 2.546% | 223 | 2.546% | 223 | 2.546% | 223 | 2.546% | 223 | 2.546% | 223 | 2.546% | 223
22 | 2.557% | 224 | 2.409% | 211 | 2.409% | 211 | 2.409% | 211 | 2.409% | 211 | 2.409% | 211 | 2.409% | 211 | 2.409% | 211 | 2.409% | 211 | 2.409% | 211 | 2.409% | 211 | 2.409% | 211
23 | 2.237% | 196 | 2.295% | 201 | 2.295% | 201 | 2.295% | 201 | 2.295% | 201 | 2.295% | 201 | 2.295% | 201 | 2.295% | 201 | 2.295% | 201 | 2.295% | 201 | 2.295% | 201 | 2.295% | 201
24 | 2.58% | 226 | 2.763% | 242 | 2.763% | 242 | 2.763% | 242 | 2.763% | 242 | 2.763% | 242 | 2.763% | 242 | 2.763% | 242 | 2.763% | 242 | 2.763% | 242 | 2.763% | 242 | 2.763% | 242
25 | 1.929% | 169 | 1.712% | 150 | 1.712% | 150 | 1.712% | 150 | 1.712% | 150 | 1.712% | 150 | 1.712% | 150 | 1.712% | 150 | 1.712% | 150 | 1.712% | 150 | 1.712% | 150 | 1.712% | 150
26 | 1.473% | 129 | 1.564% | 137 | 1.564% | 137 | 1.564% | 137 | 1.564% | 137 | 1.564% | 137 | 1.564% | 137 | 1.564% | 137 | 1.564% | 137 | 1.564% | 137 | 1.564% | 137 | 1.564% | 137
27 | 1.53% | 134 | 1.484% | 130 | 1.484% | 130 | 1.484% | 130 | 1.484% | 130 | 1.484% | 130 | 1.484% | 130 | 1.484% | 130 | 1.484% | 130 | 1.484% | 130 | 1.484% | 130 | 1.484% | 130
28 | 1.998% | 175 | 1.781% | 156 | 1.781% | 156 | 1.781% | 156 | 1.781% | 156 | 1.781% | 156 | 1.781% | 156 | 1.781% | 156 | 1.781% | 156 | 1.781% | 156 | 1.781% | 156 | 1.781% | 156
29 | 1.221% | 107 | 1.164% | 102 | 1.164% | 102 | 1.164% | 102 | 1.164% | 102 | 1.164% | 102 | 1.164% | 102 | 1.164% | 102 | 1.164% | 102 | 1.164% | 102 | 1.164% | 102 | 1.164% | 102
30 | 1.142% | 100 | 1.107% | 97 | 1.107% | 97 | 1.107% | 97 | 1.107% | 97 | 1.107% | 97 | 1.107% | 97 | 1.107% | 97 | 1.107% | 97 | 1.107% | 97 | 1.107% | 97 | 1.107% | 97
31 | 1.005% | 88 | 0.8447% | 74 | 0.8447% | 74 | 0.8447% | 74 | 0.8447% | 74 | 0.8447% | 74 | 0.8447% | 74 | 0.8447% | 74 | 0.8447% | 74 | 0.8447% | 74 | 0.8447% | 74 | 0.8447% | 74
32 | 0.8333% | 73 | 0.7877% | 69 | 0.7877% | 69 | 0.7877% | 69 | 0.7877% | 69 | 0.7877% | 69 | 0.7877% | 69 | 0.7877% | 69 | 0.7877% | 69 | 0.7877% | 69 | 0.7877% | 69 | 0.7877% | 69
33 | 0.6735% | 59 | 0.5936% | 52 | 0.5936% | 52 | 0.5936% | 52 | 0.5936% | 52 | 0.5936% | 52 | 0.5936% | 52 | 0.5936% | 52 | 0.5936% | 52 | 0.5936% | 52 | 0.5936% | 52 | 0.5936% | 52
34 | 0.468% | 41 | 0.3767% | 33 | 0.3767% | 33 | 0.3767% | 33 | 0.3767% | 33 | 0.3767% | 33 | 0.3767% | 33 | 0.3767% | 33 | 0.3767% | 33 | 0.3767% | 33 | 0.3767% | 33 | 0.3767% | 33
35 | 0.3082% | 27 | 0.3425% | 30 | 0.3425% | 30 | 0.3425% | 30 | 0.3425% | 30 | 0.3425% | 30 | 0.3425% | 30 | 0.3425% | 30 | 0.3425% | 30 | 0.3425% | 30 | 0.3425% | 30 | 0.3425% | 30
36 | 0.1826% | 16 | 0.1826% | 16 | 0.1826% | 16 | 0.1826% | 16 | 0.1826% | 16 | 0.1826% | 16 | 0.1826% | 16 | 0.1826% | 16 | 0.1826% | 16 | 0.1826% | 16 | 0.1826% | 16 | 0.1826% | 16
37 | 0.06849% | 6 | 0.03425% | 3 | 0.03425% | 3 | 0.03425% | 3 | 0.03425% | 3 | 0.03425% | 3 | 0.03425% | 3 | 0.03425% | 3 | 0.03425% | 3 | 0.03425% | 3 | 0.03425% | 3 | 0.03425% | 3
38 | 0.01142% | 1 | 0.01142% | 1 | 0.01142% | 1 | 0.01142% | 1 | 0.01142% | 1 | 0.01142% | 1 | 0.01142% | 1 | 0.01142% | 1 | 0.01142% | 1 | 0.01142% | 1 | 0.01142% | 1 | 0.01142% | 1
39 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0
40 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0
41 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0
42 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0
43 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0
44 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0
45 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0
46 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0
47 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0
48 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0
49 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0
>=50 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0

## Shear
Mean Wind Shear (power law) [α]
|  | Measurement Device |  | Wind Turbine
Wind Direction (Midpoint) (°) | Wind Speed (Midpoint) (m/s) | Gobblers Knob West | Gobblers Knob East | 97 | 98 | 100 | 102 | 103 | 104 | 105 | 106 | 107 | 108
ALL | ALL | 0.2023 | 0.14417 | 0.14417 | 0.14417 | 0.14417 | 0.14417 | 0.2023 | 0.2023 | 0.2023 | 0.2023 | 0.14417 | 0.14417
0 | ALL | 0.4043 | 0.20352 | 0.20352 | 0.20352 | 0.20352 | 0.20352 | 0.4043 | 0.4043 | 0.4043 | 0.4043 | 0.20352 | 0.20352
30 | ALL | 0.15632 | 0.13987 | 0.13987 | 0.13987 | 0.13987 | 0.13987 | 0.15632 | 0.15632 | 0.15632 | 0.15632 | 0.13987 | 0.13987
60 | ALL | 0.19544 | 0.13867 | 0.13867 | 0.13867 | 0.13867 | 0.13867 | 0.19544 | 0.19544 | 0.19544 | 0.19544 | 0.13867 | 0.13867
90 | ALL | 0.17404 | 0.13186 | 0.13186 | 0.13186 | 0.13186 | 0.13186 | 0.17404 | 0.17404 | 0.17404 | 0.17404 | 0.13186 | 0.13186
120 | ALL | 0.18529 | 0.13489 | 0.13489 | 0.13489 | 0.13489 | 0.13489 | 0.18529 | 0.18529 | 0.18529 | 0.18529 | 0.13489 | 0.13489
150 | ALL | 0.16447 | 0.13486 | 0.13486 | 0.13486 | 0.13486 | 0.13486 | 0.16447 | 0.16447 | 0.16447 | 0.16447 | 0.13486 | 0.13486
180 | ALL | 0.19338 | 0.16508 | 0.16508 | 0.16508 | 0.16508 | 0.16508 | 0.19338 | 0.19338 | 0.19338 | 0.19338 | 0.16508 | 0.16508
210 | ALL | 0.23088 | 0.21429 | 0.21429 | 0.21429 | 0.21429 | 0.21429 | 0.23088 | 0.23088 | 0.23088 | 0.23088 | 0.21429 | 0.21429
240 | ALL | 0.27011 | 0.16563 | 0.16563 | 0.16563 | 0.16563 | 0.16563 | 0.27011 | 0.27011 | 0.27011 | 0.27011 | 0.16563 | 0.16563
270 | ALL | 0.21441 | 0.13622 | 0.13622 | 0.13622 | 0.13622 | 0.13622 | 0.21441 | 0.21441 | 0.21441 | 0.21441 | 0.13622 | 0.13622
300 | ALL | 0.14458 | 0.10656 | 0.10656 | 0.10656 | 0.10656 | 0.10656 | 0.14458 | 0.14458 | 0.14458 | 0.14458 | 0.10656 | 0.10656
330 | ALL | 0.15663 | 0.078324 | 0.078324 | 0.078324 | 0.078324 | 0.078324 | 0.15663 | 0.15663 | 0.15663 | 0.15663 | 0.078324 | 0.078324

## Inflow Angle
Inflow Angle (degrees)
| Measurement Device |  | Wind Turbine
Wind Direction (Midpoint) (°) | Gobblers Knob West | Gobblers Knob East | 97 | 98 | 100 | 102 | 103 | 104 | 105 | 106 | 107 | 108
All | 0.3 | 0 | 0.1 | 0.1 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0 | 0.1 | 0.1
Max | 1.6 | 0.1 | 1.1 | 0.9 | 1.1 | 0.9 | 1.1 | 1 | 1.1 | 1.1 | 1 | 0.9
0 | 1.6 | 0 | 1.1 | 0.9 | 1.1 | 0.9 | 1.1 | 1 | 1.1 | 1.1 | 1 | 0.9
30 | -0.1 | -0.1 | 0 | 0 | 0 | 0 | -0.1 | 0 | 0 | -0.1 | 0 | -0.1
60 | 0 | 0 | 0.1 | 0 | 0 | 0 | -0.1 | 0 | 0 | 0 | 0 | 0
90 | 0.1 | -0.1 | 0.1 | 0.1 | 0.1 | 0 | 0.1 | 0.1 | -0.1 | -0.1 | -0.1 | 0
120 | 0 | 0 | 0.1 | 0 | 0.1 | -0.1 | 0 | 0 | 0 | -0.1 | 0.1 | 0.1
150 | 0 | -0.1 | 0 | -0.1 | -0.1 | 0.1 | 0 | 0.1 | 0 | 0 | -0.1 | 0
180 | 1.4 | 0 | 0 | 0 | 0 | -0.1 | 0.1 | -0.1 | -0.1 | -0.1 | 0 | 0
210 | 0 | 0 | 0 | 0.1 | 0 | -0.1 | 0 | -0.1 | 0 | -0.1 | 0.1 | 0
240 | 0 | -0.1 | -0.1 | 0 | -0.1 | 0.1 | 0.1 | 0 | 0.1 | 0.1 | 0.1 | -0.1
270 | 0 | -0.1 | -0.1 | 0 | 0 | 0 | 0 | -0.1 | 0 | 0.1 | 0.1 | 0
300 | -0.1 | 0 | 0 | 0 | 0 | -0.1 | 0 | 0.1 | 0.1 | -0.1 | 0.1 | 0
330 | 0.1 | 0 | 0 | 0.1 | -0.1 | 0 | 0.1 | 0.1 | 0.1 | -0.1 | 0.1 | 0.1

## CcT
Turbulence Structure Correction Parameter (CcT) [-1, ed 3 and ed 4]
| Measurement Device |  | Wind Turbine
| Gobblers Knob West | Gobblers Knob East | 97 | 98 | 100 | 102 | 103 | 104 | 105 | 106 | 107 | 108
sigma 3/sigma 1 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
sigma 2/sigma 1 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
CcT | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05